## Disclaimer
DISCLAIMER
Essential Energy is registered as a Distribution Network Service Provider. This Distribution Annual Planning Report 2024 has been prepared and published by Essential Energy under clause 5.12.2 and 5.13.2 of the National Electricity Rules to notify Registered Participants and Interested Parties of the results of the distribution network annual planning review and should only be used for those purposes.
This document does not purport to contain all of the information that a prospective investor, participant or potential participant in the National Electricity Market, or any other person or interested parties may require. In preparing this document it is not possible, nor is it intended, for Essential Energy to have regard to the investment objectives, financial situation and particular needs of each person who reads or uses this document.
In all cases, anyone proposing to rely on or use the information in this document should independently verify and check the accuracy, completeness, reliability and suitability of that information for their own purposes.
Accordingly, Essential Energy makes no representations or warranty as to the accuracy, reliability, completeness or suitability for particular purposes of the information in this document. Persons reading or utilising this document acknowledge that Essential Energy and their employees, agents and consultants shall have no liability (including liability to any person by reason of negligence or negligent misstatement) for any statements, opinions, information or matter (expressed or implied) arising out of, contained in or derived from, or for any omissions from, the information in this document, except in so far as liability under any New South Wales and Commonwealth statute cannot be excluded.
Contact
For all enquiries regarding the Distribution Annual Planning Report 2024 and for making written submissions contact:
Essential Energy DM Coordinator PO Box 5730 Port Macquarie NSW 2444 Email: dmcoordinator@essentialenergy.com.au

## ZSSummer
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (POE50 MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 24/25 | 25/26 | 26/27 | 27/28 | 28/29
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 33 | 1 | 13.7638 | 13.7683 | 13.7761 | 13.8072 | 13.7837 | 16.76 | 2
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 33 | 0.99969 | 15.5113 | 15.7008 | 15.8052 | 15.9117 | 16.0418 | 16.12 | 2.5
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 44 | 0.99973 | 11.4992 | 11.5672 | 11.6231 | 11.6907 | 11.7599 | 0 | 2.5
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 16.5 | 0.9999 | 11.0555 | 11.073 | 11.1621 | 11.1623 | 11.2096 | 17.1 | 2
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.99666 | 19.3913 | 19.4905 | 19.5554 | 19.6878 | 19.8133 | 23.91 | 4.5
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 220 | 0.98855 | 94.215 | 94.3838 | 94.3239 | 94.3491 | 94.4073 | 0 | 2.5
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.99804 | 6.5602 | 6.7436 | 6.9023 | 7.0988 | 7.2749 | 10.61 | 3
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 27.5 | 0.98925 | 16.383 | 16.4813 | 16.5871 | 16.6741 | 16.7857 | 5.48 | 3
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99997 | 14.2587 | 14.3078 | 14.3761 | 14.4701 | 14.5934 | 16.79 | 2
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 22 | 0.99357 | 11.4556 | 11.6881 | 11.898 | 12.0808 | 12.295 | 15.86 | 1.5
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 33 | 0.99593 | 25.9663 | 25.9596 | 25.8438 | 25.9646 | 26.0805 | 30.43 | 2
Lismore | Ballina 132kV | 132/66 | 75/112 |  |  | 0 | 0.96393 | 22.5835 | 22.6792 | 22.7029 | 22.6485 | 22.7093 | 0 | 2
Lismore | Dunoon | 132/11 | 10 | 10 |  | 11 | 0.98467 | 6.3662 | 6.4029 | 6.4358 | 6.4763 | 6.5195 | 8.05 | 3.5
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.99999 | 19.5289 | 19.8405 | 20.1558 | 20.4336 | 20.8403 | 19.45 | 2.5
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 11 | 0.98187 | 8.6184 | 8.7573 | 8.9573 | 9.0132 | 9.1699 | 7.4 | 2
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 17.6 | 0.99995 | 5.7505 | 5.9246 | 6.0773 | 6.223 | 6.4041 | 8.18 | 4.5
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 264 | 0.99917 | 77.2082 | 77.3213 | 77.9387 | 78.4148 | 78.9909 | 0 | 1
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 25.3 | 0.99594 | 16.785 | 17.1546 | 17.353 | 17.5769 | 17.8812 | 16.38 | 1.5
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 52.8 | 0.99187 | 7.7778 | 7.8044 | 7.7669 | 7.7412 | 7.7963 | 7.42 | 0.5
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 33 | 0.99541 | 19.0003 | 19.1534 | 19.3485 | 19.484 | 19.6787 | 16.68 | 2
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 11 | 0.99999 | 7.353 | 7.4677 | 7.5743 | 7.687 | 7.7774 | 11.56 | 3.5
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | 0.99911 | 11.0098 | 11.1804 | 11.3322 | 11.5133 | 11.6462 | 13.66 | 4
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 11 | 0.99925 | 7.9343 | 7.9742 | 8.0118 | 8.0454 | 8.1227 | 8.85 | 2
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 2.75 | 0.89831 | 0.90809 | 0.91424 | 0.92045 | 0.92493 | 0.93278 | 0.94 | 4
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0.98421 | 28.9956 | 29.1588 | 29.1941 | 29.2557 | 29.3347 | 0 | 4
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 33 | 0.98904 | 24.3894 | 24.3419 | 24.3287 | 24.3791 | 24.3786 | 18.79 | 6
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 3.85 | 0.99101 | 3.5915 | 3.6184 | 3.6528 | 3.6737 | 3.6979 | 0 | 3
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.99974 | 1.3479 | 1.3588 | 1.3678 | 1.3767 | 1.3887 | 0.97 | 3.5
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 5.5 | 0.99943 | 0.68618 | 0.69327 | 0.69608 | 0.69529 | 0.68926 | 0.7 | 1.5
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.99331 | 0.84471 | 0.84327 | 0.84621 | 0.84344 | 0.84823 | 0.76 | 5
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 27.5 | 0.99944 | 16.784 | 16.8416 | 16.8663 | 16.8476 | 16.8797 | 12.6 | 3
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 26.95 | 0.97556 | 17.4257 | 17.3858 | 17.3658 | 17.358 | 17.3217 | 13.79 | 1.5
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | 0.93839 | 2.2389 | 2.2535 | 2.2657 | 2.2772 | 2.3019 | 2.82 | 1
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.79027 | 9.611 | 9.6403 | 9.6489 | 9.6011 | 9.6162 | 11.73 | 8.5
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0.99073 | 0.34472 | 0.34344 | 0.34377 | 0.34326 | 0.34241 | 0 | 4
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.66 | 0.97116 | 0.22486 | 0.22586 | 0.22304 | 0.22182 | 0.22025 | 0.35 | 1.5
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.55 | 0.9925 | 0.34457 | 0.34394 | 0.34351 | 0.34302 | 0.34201 | 0.26 | 4
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | 0.9989 | 0.945 | 0.96149 | 0.99747 | 1.0413 | 1.062 | 1.18 | 2.5
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 25.3 | 0.99966 | 11.1395 | 11.2375 | 11.3628 | 11.4049 | 11.5064 | 12.47 | 3.5
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 33 | 0.99978 | 9.8336 | 9.9784 | 9.9877 | 10.0747 | 10.1339 | 9.84 | 1
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 33 | 0.99842 | 8.2941 | 8.3085 | 8.3313 | 8.3502 | 8.373 | 0 | 1
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 50.6 | 0.9984 | 22.8786 | 22.9082 | 22.8985 | 22.8618 | 22.9571 | 18.1 | 1
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99077 | 21.8915 | 22.0144 | 22.0805 | 22.1806 | 22.2736 | 12.72 | 1
Coffs Harbour | Dorrigo | 66/11, 132/11 | 7.5/10 | 10 |  | 11 | 0.99533 | 2.405 | 2.3862 | 2.3875 | 2.3756 | 2.3668 | 2.82 | 7
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 17.6 | 1 | 5.6662 | 5.8102 | 5.944 | 6.0124 | 6.1528 | 8.46 | 3
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 6.875 | 0.95376 | 3.0023 | 3.0094 | 3.0111 | 3.0093 | 3.0318 | 3.22 | 4
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 26.95 | 0.8962 | 9.296 | 9.3111 | 9.3451 | 9.306 | 9.3385 | 8.51 | 2
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.97944 | 0.38683 | 0.38834 | 0.39065 | 0.3941 | 0.39595 | 0.5 | 2
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 33 | 0.99618 | 10.1515 | 10.2843 | 10.4411 | 10.5922 | 10.7337 | 14.97 | 3
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 33 | 0.99973 | 8.9915 | 8.9904 | 9.0073 | 9.0415 | 9.0924 | 10.88 | 2.5
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 25.3 | 0.99303 | 7.3406 | 7.397 | 7.4759 | 7.5697 | 7.6354 | 8.88 | 4.5
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 33 | 0.99035 | 9.3687 | 9.3644 | 9.3797 | 9.3712 | 9.3772 | 11.87 | 4.5
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.4 | 0.9963 | 1.5532 | 1.547 | 1.5458 | 1.5461 | 1.5443 | 1.72 | 9
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.99754 | 1.5168 | 1.514 | 1.5149 | 1.5217 | 1.5165 | 1.53 | 2
Kempsey | North St | 33/11 | 10 | 16 |  | 11 | 0.99186 | 11.5478 | 11.6245 | 11.7535 | 11.7926 | 11.9 | 8.02 | 4
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 16.5 | 0.97819 | 8.1185 | 8.1853 | 8.2121 | 8.2643 | 8.3436 | 7.06 | 1.5
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 5.5 | 0.98457 | 4.3617 | 4.4196 | 4.5145 | 4.5637 | 4.6425 | 2.76 | 1
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 13.75 | 0.99897 | 6.3463 | 6.3902 | 6.4465 | 6.4876 | 6.53 | 7.66 | 4
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 33 | 0.99988 | 20.6693 | 20.9833 | 21.3886 | 21.7389 | 22.1484 | 13.88 | 3
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.99018 | 1.3688 | 1.3593 | 1.3579 | 1.3626 | 1.3595 | 1.33 | 2
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 33 | 0.99975 | 19.8105 | 19.9823 | 20.2857 | 20.4576 | 20.6683 | 26.78 | 2.5
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 3.85 | 0.99914 | 2.6069 | 2.6713 | 2.7479 | 2.8108 | 2.8752 | 2.91 | 2
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 8.8 | 0.99397 | 5.2375 | 5.3286 | 5.4327 | 5.4991 | 5.5876 | 9.13 | 1
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 22 | 0.98735 | 14.3842 | 14.3552 | 14.3253 | 14.3278 | 14.3239 | 7.41 | 3.5
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 16.5 | 0.99394 | 11.8002 | 11.7618 | 11.7546 | 11.8642 | 11.8222 | 12.6 | 1
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.4 | 0.99986 | 1.8377 | 1.855 | 1.8669 | 1.8962 | 1.9197 | 2.08 | 1.5
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0.99819 | 10.6959 | 10.6581 | 10.6501 | 10.6545 | 10.65 | 0 | 2.5
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | 0.95302 | 0.83858 | 0.83697 | 0.83434 | 0.83516 | 0.83602 | 1.01 | 3
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.4 | 0.9996 | 3.5322 | 3.5546 | 3.5994 | 3.6416 | 3.6804 | 4.9 | 1
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 22 | 0.99995 | 7.7159 | 7.7299 | 7.7308 | 7.7377 | 7.7675 | 8.61 | 1
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 7.7 | 0.99238 | 6.0254 | 6.1608 | 6.3158 | 6.4519 | 6.5849 | 7.63 | 2
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 5.5 | 0.98404 | 3.8958 | 3.9264 | 3.9587 | 3.9844 | 4.0153 | 1.78 | 3
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.99369 | 2.7581 | 2.7814 | 2.8048 | 2.8557 | 2.8917 | 2.8 | 4.5
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.99812 | 14.5173 | 14.621 | 14.6431 | 14.7684 | 14.8088 | 13.91 | 2.5
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.99807 | 7.1337 | 7.1656 | 7.1473 | 7.1738 | 7.1953 | 9.98 | 2.5
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 6.875 | 1 | 3.2121 | 3.2624 | 3.3062 | 3.366 | 3.418 | 4.83 | 2
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 27.5 | 0.99928 | 9.1649 | 9.052 | 8.8974 | 8.7922 | 8.7051 | 8.6 | 4
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 17.6 | 0.99912 | 5.7951 | 5.9095 | 6.0727 | 6.1974 | 6.2087 | 4.89 | 3.5
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 22 | 0.99484 | 18.0836 | 17.9672 | 17.8483 | 17.8558 | 17.865 | 10.33 | 4
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 11 | 0.97597 | 11.4366 | 11.5442 | 11.6215 | 11.7472 | 11.8303 | 8.01 | 1.5
Stroud | Booral | 33/11 | 3 | 2.5 |  | 2.75 | 0.96141 | 1.5985 | 1.6039 | 1.5996 | 1.5898 | 1.6039 | 1.24 | 2
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.95857 | 3.958 | 4.0051 | 4.0344 | 4.0887 | 4.1202 | 2.82 | 1.5
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.98996 | 8.6235 | 8.7137 | 8.7995 | 8.9056 | 8.9859 | 5.94 | 1
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.99537 | 8.6386 | 8.6433 | 8.6843 | 8.7048 | 8.6741 | 6.76 | 1
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.95882 | 2.4336 | 2.432 | 2.4103 | 2.4071 | 2.4078 | 1.69 | 3.5
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.98841 | 3.6522 | 3.6766 | 3.696 | 3.7213 | 3.7413 | 2.81 | 2
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.99988 | 4.0045 | 4.009 | 3.9874 | 4.0004 | 4.0004 | 3.95 | 3
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 66 | 0.99588 | 35.3827 | 35.6239 | 35.8151 | 36.0458 | 36.4757 | 0.01 | 1.5
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 5.5 | 0.98472 | 2.8323 | 2.853 | 2.8536 | 2.8652 | 2.8847 | 2.08 | 1.5
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0.99789 | 8.6151 | 8.6815 | 8.6896 | 8.7344 | 8.8044 | 0 | 3.5
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.99974 | 9.2865 | 9.329 | 9.366 | 9.3706 | 9.3558 | 7.63 | 2.5
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply | [5 empty] | 0.98937 | 4.2357 | 4.2781 | 4.2974 | 4.3173 | 4.3459 | 2.74 | 3
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 2.75 | 0.99965 | 1.6776 | 1.6935 | 1.7114 | 1.7313 | 1.7517 | 1.9 | 2
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 13.75 | 0.99598 | 9.5299 | 9.6839 | 9.8345 | 9.9068 | 10.1073 | 9.46 | 2
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.95772 | 0.54741 | 0.54872 | 0.54965 | 0.55794 | 0.57785 | 0.22 | 3
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 13.75 | 0.99561 | 7.8183 | 7.8593 | 7.8965 | 7.9378 | 7.9904 | 6.32 | 3
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.99942 | 7.0464 | 7.0704 | 7.0993 | 7.1873 | 7.277 | 6.1 | 4
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 3.85 | 0.95334 | 0.39648 | 0.39967 | 0.40232 | 0.40498 | 0.40952 | 0.23 | 2
Armidale | Uralla | 66/11 | 8 | 5 |  | 5.5 | 0.95559 | 3.0146 | 3.0139 | 3.0119 | 3.0317 | 3.0283 | 3.57 | 4
Armidale | Walcha South 66/22kV | 66/22 | 8 | 8/10 |  | 8.8 | 0.73949 | 1.6954 | 1.7225 | 1.7487 | 1.7838 | 1.8086 | 1.06 | 4
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.3 | 0.9987 | 1.3572 | 1.3567 | 1.3569 | 1.344 | 1.3532 | 1.24 | 4
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.95546 | 0.69295 | 0.68779 | 0.69059 | 0.69112 | 0.68543 | 1.29 | 3
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | 0.70583 | 0.14754 | 0.14695 | 0.14803 | 0.1476 | 0.14763 | 0.13 | 1.5
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 22 | 0.99838 | 6.0915 | 6.0958 | 6.1 | 6.0943 | 6.1011 | 6.95 | 7
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 5.5 | 0.99985 | 3.8426 | 3.8994 | 4.0114 | 4.0916 | 4.157 | 3.36 | 5
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0.99999 | 0.0040229 | 0.0041578 | 0.0043105 | 0.0044668 | 0.0045323 | 0.01 | 0
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.94704 | 0.71791 | 0.71876 | 0.72446 | 0.72567 | 0.72845 | 0.84 | 4
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.3 | 0.99133 | 2.487 | 2.4998 | 2.5193 | 2.5469 | 2.562 | 2.2 | 4
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 33 | 0.99914 | 20.0807 | 19.9221 | 19.9452 | 19.9233 | 20.0072 | 16 | 2.5
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | 0.57396 | 1.3149 | 1.3447 | 1.3743 | 1.4053 | 1.4324 | 0.77 | 3
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.65 | 0.9539 | 0.86332 | 0.86349 | 0.86203 | 0.86564 | 0.86446 | 0 | 3
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 5.5 | 0.95195 | 3.43 | 3.4317 | 3.424 | 3.4313 | 3.4299 | 1.51 | 1
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 5.5 | 0.95151 | 1.8375 | 1.8399 | 1.8368 | 1.8389 | 1.8373 | 0.61 | 2.5
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | 0.86892 | 0.18515 | 0.18608 | 0.18806 | 0.18881 | 0.19029 | 0.13 | 1
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.4 | 0.99593 | 3.0333 | 3.0444 | 3.0624 | 3.0764 | 3.0867 | 2.39 | 3.5
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.9517 | 2.1911 | 2.202 | 2.1995 | 2.2096 | 2.2155 | 0.94 | 5
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 16.5 | 0.99807 | 14.7229 | 14.8321 | 14.8144 | 14.9101 | 14.9747 | 7.04 | 5
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.99398 | 5.308 | 5.3269 | 5.3646 | 5.4152 | 5.4619 | 2.92 | 6
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.98732 | 2.6361 | 2.645 | 2.6029 | 2.6941 | 2.657 | 0.55 | 9
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 2.75 | 0.94938 | 1.1423 | 1.1475 | 1.1461 | 1.15 | 1.1547 | 0.56 | 6
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 33 | 0.99793 | 21.5394 | 21.8773 | 24.1899 | 28.9841 | 33.3853 | 14.26 | 6
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.9545 | 2.6387 | 2.6484 | 2.6516 | 2.6661 | 2.6682 | 1.29 | 9
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.95511 | 4.1844 | 4.2087 | 4.209 | 4.211 | 4.226 | 0.23 | 0.5
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | 0.90187 | 2.7613 | 2.8527 | 2.8605 | 2.9016 | 2.9622 | 0.09 | 19
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.97058 | 2.852 | 2.8914 | 2.9177 | 2.9648 | 2.9866 | 1.28 | 2
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 5.5 | 0.99496 | 2.1135 | 2.1153 | 2.1067 | 2.1053 | 2.1024 | 0.76 | 2
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 5.5 | 0.99998 | 3.1595 | 3.1755 | 3.1909 | 3.2107 | 3.2295 | 2.57 | 9
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0.85659 | 1.5275 | 1.5469 | 1.5677 | 1.5886 | 1.6014 | 0.7 | 2.5
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.99575 | 15.2996 | 15.2536 | 15.2417 | 15.2453 | 15.2988 | 10.71 | 2
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 11 | 0.9817 | 5.2416 | 5.2871 | 5.3288 | 5.3388 | 5.423 | 3.26 | 4
Narrabri | Wee Waa | 66/22 | 10 | 16 |  | 11 | 0.94477 | 7.3852 | 7.3856 | 7.4123 | 7.3839 | 7.3941 | 3.15 | 8
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.15 | 0.99893 | 3.2597 | 3.2556 | 3.2511 | 3.2777 | 3.2607 | 1.83 | 6
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.98872 | 25.0299 | 25.0412 | 25.1553 | 25.1927 | 25.2701 | 13.31 | 3.5
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0.97891 | 0.28371 | 0.27899 | 0.27984 | 0.27437 | 0.27901 | 0.03 | 3
Tamworth | Attunga | 66/11 | 5 | 8 |  | 5.5 | 0.95461 | 3.4321 | 3.4326 | 3.4446 | 3.4278 | 3.4407 | 1.77 | 4
Tamworth | Barraba | 66/11 | 5 | 5 |  | 5.5 | 0.99918 | 2.2759 | 2.2663 | 2.272 | 2.2767 | 2.277 | 2.12 | 2
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.1 | 0.99721 | 0.70044 | 0.7039 | 0.70603 | 0.71028 | 0.71775 | 0.64 | 2
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.2 | 0.96963 | 0.96381 | 0.96173 | 0.96265 | 0.96066 | 0.96278 | 0.15 | 1
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.65 | 0.94044 | 1.2561 | 1.2705 | 1.279 | 1.2919 | 1.3015 | 0.42 | 6
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.95267 | 1.279 | 1.2788 | 1.2707 | 1.2688 | 1.2603 | 0.6 | 4
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 33 | 1 | 11.635 | 11.6392 | 19.7513 | 21.5751 | 23.1521 | 4.26 | 4.5
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.9908 | 6.0536 | 6.1025 | 6.1392 | 6.1952 | 6.2462 | 4.75 | 1.5
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.89651 | 5.0849 | 5.1087 | 5.1174 | 5.1228 | 5.1335 | 3.21 | 3
Tamworth | Murrurundi | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.99794 | 2.774 | 2.7752 | 2.7891 | 2.791 | 2.7835 | 2.04 | 3
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 2.75 | 0.9697 | 1.4718 | 1.4547 | 1.4286 | 1.4163 | 1.4016 | 1.28 | 3
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 33 | 0.99633 | 19.3431 | 19.5319 | 19.7769 | 19.9471 | 20.2719 | 13.56 | 1.5
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.99994 | 6.4655 | 6.4633 | 6.4617 | 6.5019 | 6.5207 | 4.71 | 2
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 11 | 0.99148 | 5.0687 | 5.0749 | 5.0851 | 5.0734 | 5.1171 | 0 | 4.5
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.97724 | 0.6407 | 0.64663 | 0.65347 | 0.65858 | 0.66833 | 0.19 | 6
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 50.6 | 0.99126 | 30.9675 | 30.9456 | 30.9665 | 30.8996 | 31.1105 | 14.27 | 2.5
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99431 | 23.3806 | 23.355 | 23.344 | 23.2877 | 23.3055 | 14.99 | 3.5
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.94371 | 0.704 | 0.6982 | 0.68752 | 0.67971 | 0.674 | 0.12 | 4.5
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 6.875 | 0.94925 | 2.5978 | 2.5986 | 2.605 | 2.6148 | 2.6213 | 1.45 | 2
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 14.3 | 0.99998 | 8.1447 | 8.1386 | 8.1389 | 8.1381 | 8.155 | 6.88 | 3
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 11 | 0.99545 | 5.0103 | 5.0026 | 4.9836 | 4.9824 | 4.9677 | 4.26 | 6
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | 0.99906 | 2.9209 | 2.9213 | 2.9275 | 2.9506 | 2.9622 | 2.38 | 2
Beryl | Mudgee | 66/22, 132/22 | 18/30 | 30 |  | 33 | 0.99636 | 22.7811 | 22.8757 | 22.7962 | 22.8259 | 22.8102 | 18.48 | 4.5
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 2.75 | 0.95253 | 2.4072 | 2.4115 | 2.4163 | 2.4214 | 2.4214 | 1.67 | 2
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 2.75 | 0.95584 | 1.3653 | 1.3715 | 1.3972 | 1.4123 | 1.4323 | 0.89 | 4
Wellington | Wellington 11kV | 132/11, 66/11 | 10 | 15 |  | 11 | 0.98674 | 8.9765 | 8.9468 | 8.9824 | 9.0115 | 9.0151 | 5.49 | 5
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 11 | 0.99553 | 5.9793 | 6.0312 | 6.0764 | 6.1197 | 6.1677 | 3.61 | 4
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 99 | 0.98326 | 57.7809 | 57.6567 | 57.8169 | 57.6762 | 57.7429 | 0 | 5
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 33 | 0.97221 | 20.3912 | 20.2518 | 20.0884 | 19.9701 | 19.9669 | 7.27 | 2
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 33 | 0.99832 | 18.1453 | 18.3635 | 18.5874 | 18.7599 | 19.0088 | 15.49 | 1.5
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 25.3 | 0.98785 | 15.2378 | 15.3889 | 15.5555 | 15.7119 | 15.9113 | 12.29 | 3.5
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 33 | 0.99477 | 18.9113 | 18.9063 | 19.0084 | 19.0218 | 19.1032 | 17.92 | 2.5
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | 0.98287 | 1.4974 | 1.5145 | 1.5129 | 1.5155 | 1.5221 | 1.21 | 4
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 13.2 | 0.99384 | 6.9373 | 6.9676 | 6.9841 | 7.0456 | 7.0532 | 4.82 | 2
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.95336 | 1.6496 | 1.6548 | 1.6593 | 1.6639 | 1.6715 | 1.01 | 1.5
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 26.4 | 0.99864 | 12.2521 | 12.2122 | 12.2801 | 12.2761 | 12.1871 | 8.35 | 3
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 11 | 0.92258 | 6.7229 | 6.7108 | 6.7553 | 6.7654 | 6.7728 | 3.64 | 2
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 27.5 | 0.96673 | 7.6321 | 7.6362 | 7.6496 | 7.6393 | 7.6372 | 2.15 | 13
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.99996 | 5.3527 | 5.4139 | 5.4766 | 5.5366 | 5.6012 | 2.54 | 9
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.81263 | 3.1411 | 3.2007 | 3.2632 | 3.3259 | 3.3875 | 0.79 | 2
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.1 | 0.99497 | 0.11423 | 0.11515 | 0.11486 | 0.1148 | 0.11518 | 0.04 | 1
Nyngan | Cobar CSA | 132/11 | 15/18 |  |  | 0 | 0.98609 | 22.0996 | 22.5116 | 22.8172 | 23.2939 | 23.7231 | 0 | 7
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 16.5 | 0.9032 | 2.1089 | 2.1531 | 2.1735 | 2.2009 | 2.1928 | 0 | 1
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 22 | 0.94112 | 15.6825 | 15.738 | 15.9119 | 15.9686 | 16.073 | 0 | 129
Nyngan | Cobar Town | 66/22 | 8/11 | 10/13 |  | 12.1 | 0.95688 | 6.2125 | 6.1387 | 6.083 | 6.0495 | 5.997 | 5.25 | 5
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0.90948 | 3.1463 | 3.1918 | 3.1938 | 3.2267 | 3.2444 | 0 | 23
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 33 | 0.99929 | 30.5824 | 30.6057 | 30.6072 | 30.6322 | 30.6861 | 0 | 14
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 11 | 0.99757 | 7.5002 | 7.4474 | 7.4136 | 7.3894 | 7.4113 | 2.91 | 2.5
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply | [5 empty] | 0.99481 | 38.6841 | 40.2214 | 40.2328 | 40.1127 | 40.0978 | 25.4 | 4
Broken Hill | Wilcannia 33kV | [5 empty] | 0.88211 | 0.65162 | 0.66806 | 0.68744 | 0.70285 | 0.72136 | 0.36 | 4.5
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 5.5 | 0.99809 | 0.88265 | 0.88778 | 0.89355 | 0.90264 | 0.91015 | 1.06 | 2.5
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.65 | 0.88296 | 1.3389 | 1.3625 | 1.3876 | 1.4022 | 1.426 | 0.93 | 9
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.65 | 0.9971 | 0.61742 | 0.62263 | 0.6201 | 0.6267 | 0.63297 | 0.21 | 161
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 16.5 | 0.90001 | 6.383 | 7.531 | 7.589 | 7.6932 | 7.7829 | 0 | 5.5
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | 0.97317 | 0.62649 | 0.63856 | 0.62802 | 0.64884 | 0.6558 | 0.37 | 3
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.4 | 0.97274 | 2.1408 | 2.1278 | 2.1231 | 2.1144 | 2.1256 | 0.24 | 5
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 3.85 | 0.97557 | 0.93008 | 0.94602 | 0.95939 | 0.97039 | 0.98632 | 0.67 | 3.5
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 11 | 0.99988 | 10.3231 | 10.3642 | 10.4718 | 10.642 | 10.6638 | 12.01 | 6
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 33 | 0.95135 | 13.9432 | 13.964 | 13.9334 | 13.8693 | 13.9177 | 8.27 | 4
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99695 | 17.7726 | 18.1345 | 18.6269 | 19.0686 | 19.6196 | 13.83 | 4
Orange | Orange West | 66/11 | 30 | 30 |  | 33 | 1 | 12.5645 | 12.5019 | 12.4672 | 12.3417 | 12.3214 | 12.21 | 4
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 2.75 | 0.9476 | 2.3524 | 2.3954 | 2.4438 | 2.4493 | 2.4994 | 1.57 | 1.5
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 26.4 | 0.96691 | 9.8526 | 9.8695 | 9.8654 | 9.8776 | 9.9 | 2.12 | 10
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.4 | 0.999 | 3.4747 | 3.5082 | 3.4901 | 3.5213 | 3.5227 | 2.89 | 2
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 22 | 0.98755 | 10.0923 | 10.1827 | 10.2183 | 10.273 | 10.3952 | 5.62 | 2
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 2.75 | 0.99743 | 2.1592 | 2.1627 | 2.1664 | 2.1706 | 2.1733 | 1.94 | 1.5
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 33 | 0.99986 | 18.8545 | 18.7283 | 18.8071 | 18.7725 | 18.8616 | 13.13 | 2.5
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 66 | 0.99834 | 19.1231 | 19.1833 | 19.1718 | 19.2529 | 19.203 | 11.93 | 2.5
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 22 | 0.9998 | 18.4355 | 18.5227 | 18.8238 | 18.6442 | 18.7889 | 15.17 | 2
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0.82654 | 0.44998 | 0.44812 | 0.44867 | 0.45011 | 0.45092 | 0 | 1.5
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 49.5 | 0.91 | 32.1088 | 33.0127 | 33.918 | 34.9009 | 35.8823 | 0 | 28
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 16.5 | 0.99992 | 5.0848 | 5.199 | 5.309 | 5.445 | 5.5707 | 4.23 | 3.5
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 33 | 0.99436 | 18.5057 | 18.6452 | 18.7751 | 18.8844 | 18.9952 | 12.99 | 2
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 11 | 0.99902 | 1.6677 | 1.665 | 1.6667 | 1.665 | 1.6657 | 1.68 | 1.5
Parkes | Trundle | 66/22 | 8 | 5 |  | 5.5 | 0.99325 | 3.6795 | 3.6635 | 3.6232 | 3.6948 | 3.634 | 2.36 | 7
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 11 | 0.99986 | 7.0323 | 7.0143 | 7.0431 | 7.0351 | 7.0545 | 5.31 | 6
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 33 | 0.99207 | 13.9883 | 14.034 | 14.0757 | 14.1163 | 14.1487 | 9.14 | 7
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 7.7 | 0.99968 | 3.6824 | 3.693 | 3.7131 | 3.7349 | 3.7291 | 3.19 | 5.5
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 5.5 | 0.95621 | 5.8119 | 5.8549 | 5.8205 | 5.8174 | 5.8008 | 1.34 | 3.5
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.4 | 0.98342 | 2.095 | 2.0934 | 2.0808 | 2.0707 | 2.0681 | 0.45 | 3
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.9998 | 19.9095 | 19.9474 | 20.0644 | 20.1102 | 20.1939 | 14.07 | 2
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.3 | 0.99464 | 1.1818 | 1.1772 | 1.1722 | 1.1714 | 1.1742 | 1.35 | 2
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 44 | 0.99721 | 21.887 | 22.1197 | 22.4086 | 22.5889 | 22.8669 | 0 | 5
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.99834 | 6.0236 | 6.0296 | 6.0082 | 6.0138 | 6.0464 | 6.43 | 5.5
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 13.75 | 0.99851 | 6.7446 | 6.8437 | 6.892 | 6.9685 | 7.0112 | 8.25 | 3
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 13.75 | 0.99992 | 5.9617 | 5.9862 | 6.0015 | 6.0268 | 6.0707 | 6 | 3.5
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | 0.99888 | 1.9845 | 1.972 | 1.9503 | 1.9423 | 1.9442 | 2.8 | 6
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 5.5 | 0.99831 | 0.99177 | 1.0092 | 1.0285 | 1.0436 | 1.0637 | 0.72 | 2.5
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 5.5 | 0.78497 | 0.088684 | 0.089341 | 0.090666 | 0.088573 | 0.090103 | 0 | 28
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 22 | 0.99451 | 10.2849 | 10.2765 | 10.2638 | 10.2603 | 10.2602 | 7.22 | 1.5
Cooma | Eucumbene | 66/11 | 0.6 |  |  | 0 | 0.95691 | 0.13884 | 0.13873 | 0.1389 | 0.13861 | 0.13891 | 0.08 | 4
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 33 | 0.99238 | 4.5366 | 4.5357 | 4.527 | 4.5353 | 4.5273 | 3.98 | 3
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0.95331 | 0.37361 | 0.38697 | 0.39631 | 0.41195 | 0.42368 | 0.26 | 1
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 11 | 0.99964 | 2.2797 | 2.3354 | 2.3904 | 2.4418 | 2.5056 | 2.84 | 2
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 0.86859 | 0.13505 | 0.13315 | 0.13533 | 0.13363 | 0.13155 | 0 | 1
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.99201 | 0.49196 | 0.50293 | 0.52033 | 0.51972 | 0.51457 | 0 | 1
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 1 | 0.48571 | 0.50149 | 0.51306 | 0.52546 | 0.53933 | 0.2 | 3
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 0.99956 | 0.50072 | 0.4891 | 0.4934 | 0.48426 | 0.48752 | 0 | 19.5
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 11 | 0.95435 | 1.2539 | 1.2854 | 1.309 | 1.3193 | 1.3411 | 0.12 | 13
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0.60314 | 0.031229 | 0.031106 | 0.032681 | 0.032916 | 0.033035 | 0 | 1
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0.99616 | 3.017 | 3.0027 | 3.0973 | 3.0546 | 3.1516 | 0 | 2
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.98968 | 2.1841 | 2.2041 | 2.2242 | 2.2426 | 2.2672 | 0.03 | 3
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.99952 | 31.9597 | 31.9642 | 31.9824 | 32.0451 | 32.0076 | 0 | 3
Bega | Bermagui | 33/11 | 5 | 5 |  | 5.5 | 0.99857 | 2.6225 | 2.6259 | 2.6278 | 2.6295 | 2.6312 | 3.14 | 2.5
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0.97425 | 0.7138 | 0.71683 | 0.7159 | 0.71712 | 0.72008 | 0.57 | 2
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 2.75 | 1 | 1.1979 | 1.1983 | 1.1958 | 1.2062 | 1.2083 | 1.97 | 4.5
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.99965 | 4.0308 | 4.0325 | 4.0298 | 4.0295 | 4.036 | 3.47 | 2
Bega | Edrom | 66/11 | 5 | 5 |  | 5.5 | 0.89717 | 2.3464 | 2.3518 | 2.3489 | 2.3652 | 2.3701 | 0 | 4.5
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0.99976 | 4.3037 | 4.3183 | 4.3243 | 4.3475 | 4.3705 | 0 | 6.5
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.98881 | 13.7981 | 13.8479 | 13.8562 | 13.9073 | 13.963 | 10.39 | 3.5
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 17.6 | 0.99984 | 11.5498 | 11.5349 | 11.5322 | 11.5027 | 11.4937 | 12.92 | 2.5
Bega | Quira | 66/11 | 5 |  |  | 0 | 0.99136 | 1.1994 | 1.1994 | 1.2043 | 1.1936 | 1.1939 | 1.16 | 4
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 14.3 | 0.99776 | 4.2675 | 4.2772 | 4.2817 | 4.2923 | 4.283 | 1.55 | 7.5
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | 0.99771 | 4.8556 | 4.8717 | 4.8698 | 4.907 | 4.8963 | 0 | 3
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.96779 | 0.70707 | 0.71719 | 0.72671 | 0.7377 | 0.74907 | 0.49 | 8.5
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 2.75 | 0.99811 | 1.3628 | 1.3739 | 1.3662 | 1.3707 | 1.359 | 1.46 | 1
Tumut | Batlow | 66/11 | 5 | 5 |  | 5.5 | 0.99162 | 1.5967 | 1.5821 | 1.5831 | 1.5813 | 1.5835 | 1.34 | 5
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 8.8 | 0.99742 | 5.9272 | 5.9404 | 5.9506 | 5.9515 | 5.9806 | 3.86 | 3
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.1 | 0.9992 | 1.0537 | 1.0502 | 1.0535 | 1.0501 | 1.0537 | 0.55 | 4
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.99987 | 0.096382 | 0.09576 | 0.095627 | 0.094674 | 0.094707 | 0.08 | 1
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | 0.8837 | 0.55705 | 0.57977 | 0.60034 | 0.62268 | 0.65683 | 0.36 | 1
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 8.8 | 0.99833 | 7.6509 | 7.6541 | 7.6739 | 7.6944 | 7.7003 | 3.34 | 3
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 33 | 0.97534 | 12.8521 | 12.7434 | 12.7114 | 12.6702 | 12.5417 | 7.62 | 1
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0.99996 | 7.8579 | 7.958 | 7.9995 | 8.0017 | 8.0569 | 9.5 | 3.5
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 5.5 | 0.99978 | 6.5275 | 6.928 | 7.2478 | 7.6305 | 7.9431 | 3.57 | 9
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 11 | 0.98811 | 0.76151 | 0.76028 | 0.75309 | 0.75671 | 0.7562 | 0 | 1
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 33 | 0.99771 | 8.3324 | 8.5897 | 8.8222 | 9.0588 | 9.3601 | 13.42 | 3
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 33 | 0.99668 | 12.4593 | 12.4093 | 12.3964 | 12.4025 | 12.4058 | 9.56 | 3
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 33 | 0.99957 | 16.3497 | 16.6899 | 16.8496 | 17.2763 | 17.4324 | 19.66 | 3
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 8.8 | 0.9946 | 3.7077 | 3.7153 | 3.7331 | 3.7434 | 3.7705 | 4.79 | 3
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 2.75 | 0.96555 | 2.353 | 2.3782 | 2.3845 | 2.397 | 2.4373 | 2.62 | 2.5
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 20.9 | 0.98861 | 12.613 | 12.7023 | 12.7943 | 12.9714 | 13.2477 | 8.87 | 3.5
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0.99983 | 3.7908 | 3.7881 | 3.7953 | 3.8233 | 3.8269 | 4.61 | 3
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 33 | 0.99975 | 8.3708 | 8.3498 | 8.3504 | 8.4052 | 8.3859 | 4.72 | 4.5
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.99423 | 32.2488 | 32.5271 | 33.0164 | 33.1606 | 33.8344 | 0 | 1
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 16.5 | 0.99965 | 7.7616 | 7.7944 | 7.7681 | 7.7043 | 7.7501 | 8.54 | 1.5
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 16.5 | 0.9926 | 6.3289 | 6.352 | 6.4141 | 6.4644 | 6.5457 | 3.01 | 3
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.95934 | 7.5415 | 7.5531 | 7.5855 | 7.5726 | 7.6071 | 0 | 4
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 15.4 | 0.99939 | 7.81 | 7.8605 | 7.8631 | 7.8953 | 7.8648 | 1.42 | 14.5
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | 0.95625 | 1.7044 | 1.7168 | 1.7225 | 1.729 | 1.7452 | 1.44 | 1
Cowra | Canowindra | 66/11 | 5 | 8 |  | 5.5 | 0.98836 | 5.8609 | 5.8805 | 5.8777 | 5.8966 | 5.9428 | 3.88 | 5
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 33 | 0.99601 | 19.2267 | 19.2616 | 19.2901 | 19.4204 | 19.4501 | 12.74 | 3.5
Cowra | Grenfell | 66/11 | 8 | 5 |  | 5.5 | 0.95284 | 4.4164 | 4.416 | 4.4087 | 4.4159 | 4.4126 | 4.22 | 2.5
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.96516 | 0.86287 | 0.86075 | 0.85825 | 0.8529 | 0.84893 | 0.68 | 2
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 5.5 | 0.98609 | 3.4813 | 3.4965 | 3.5077 | 3.5288 | 3.5486 | 3.09 | 1.5
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 20.9 | 0.99978 | 9.3233 | 9.2891 | 9.2767 | 9.2705 | 9.3691 | 7.8 | 3
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.15 | 0.96224 | 1.6656 | 1.6818 | 1.6926 | 1.7052 | 1.7213 | 0.43 | 5
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 11 | 0.99098 | 4.4161 | 4.3701 | 4.3579 | 4.3555 | 4.3469 | 3.94 | 4.5
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 33 | 0.99804 | 15.9571 | 15.8835 | 15.9356 | 15.9376 | 15.893 | 10.62 | 3
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 2.75 | 0.99944 | 1.1181 | 1.1227 | 1.1251 | 1.131 | 1.136 | 1.31 | 2
Yass | Marilba | 66/11 | 3 |  |  | 0 | 0.99938 | 1.399 | 1.415 | 1.4216 | 1.4296 | 1.4392 | 1.3 | 2.5
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | 0.99628 | 6.1167 | 6.2534 | 6.4009 | 6.4656 | 6.5791 | 8.78 | 3
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 14.3 | 0.97062 | 12.1441 | 12.1922 | 12.2539 | 12.3973 | 12.4023 | 10 | 3
Temora | Anona | 66/22 | 3 | 2.5 |  | 2.75 | 0.9759 | 1.3191 | 1.3401 | 1.357 | 1.3738 | 1.3921 | 0.99 | 3.5
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 2.75 | 0.98555 | 0.77996 | 0.78052 | 0.77881 | 0.78321 | 0.78237 | 0.64 | 3
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.3 | 0.99886 | 1.0054 | 1.0065 | 1.0229 | 1.0257 | 1.0314 | 0.74 | 4
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | 0.98452 | 0.19465 | 0.19727 | 0.20041 | 0.20483 | 0.20915 | 0.17 | 2.5
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.99855 | 18.8968 | 19.0564 | 19.0474 | 19.1513 | 19.2189 | 0 | 4
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 11 | 0.99915 | 7.1271 | 7.099 | 7.111 | 7.0972 | 7.1469 | 6.3 | 5
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 11 | 0.9718 | 8.0448 | 8.069 | 8.0828 | 8.1238 | 8.1346 | 5.63 | 2
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.3 | 0.99976 | 0.70625 | 0.70531 | 0.70411 | 0.70153 | 0.70132 | 0.29 | 8
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 33 | 0.99406 | 11.0699 | 11.0761 | 13.4057 | 15.7514 | 18.0789 | 0.3 | 35.5
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/10 | 6.75/10 |  | 11 | 0.99893 | 8.6522 | 8.7926 | 8.9414 | 9.0974 | 9.2431 | 5.49 | 2.5
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.4 | 0.98693 | 1.7272 | 1.7138 | 1.7172 | 1.7115 | 1.7175 | 0 | 3
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 8.8 | 0.99309 | 4.6297 | 4.6212 | 4.6371 | 4.628 | 4.6273 | 4.35 | 7
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.3 | 0.95513 | 1.2291 | 1.2253 | 1.2261 | 1.2293 | 1.2259 | 0.85 | 4
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 15.4 | 0.99214 | 4.9306 | 4.9222 | 4.8914 | 4.8986 | 4.9028 | 2.75 | 2
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | 0.9887 | 0.47139 | 0.46033 | 0.45283 | 0.44355 | 0.43775 | 0.24 | 3
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 16.5 | 0.99664 | 6.6828 | 6.7069 | 6.7089 | 6.7119 | 6.707 | 4.07 | 8
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | 0.99995 | 11.571 | 11.6171 | 11.6016 | 11.6489 | 11.6663 | 0 | 2
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.99839 | 0.46388 | 0.46159 | 0.45849 | 0.46063 | 0.46327 | 0.39 | 2
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.2 | 0.99555 | 1.632 | 1.6404 | 1.6608 | 1.6733 | 1.691 | 0 | 4.5
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 7.59 | 0.97993 | 3.6649 | 3.6508 | 3.6517 | 3.6552 | 3.6417 | 0.59 | 6
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.1 | 0.90659 | 1.0405 | 1.0398 | 1.035 | 1.0362 | 1.0297 | 0.81 | 4
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 33 | 0.99105 | 18.1566 | 18.1071 | 18.0705 | 18.0158 | 17.994 | 11.61 | 6
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.99792 | 11.9495 | 12.0711 | 12.1194 | 12.1889 | 12.3042 | 10.29 | 3
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0.99485 | 0.16137 | 0.16385 | 0.16151 | 0.16222 | 0.16205 | 0 | 5
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 33 | 0.99958 | 14.3437 | 14.3228 | 14.3025 | 14.3893 | 14.285 | 5.1 | 10
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 5.5 | 0.9956 | 2.3755 | 2.3874 | 2.4045 | 2.4281 | 2.4303 | 2.12 | 5
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 27.5 | 0.99301 | 17.5776 | 17.7856 | 18.1263 | 18.2914 | 18.6713 | 13.19 | 4
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 5.5 | 0.99017 | 3.2818 | 3.2819 | 3.2946 | 3.3036 | 3.3147 | 2.52 | 5
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 22 | 0.98541 | 11.2359 | 11.1436 | 11.1017 | 11.1184 | 11.0939 | 2.82 | 4
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 17.6 | 0.99919 | 5.5679 | 5.5817 | 5.5965 | 5.6053 | 5.6002 | 3.56 | 3
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 7.7 | 0.98745 | 3.7923 | 3.7968 | 3.8073 | 3.8097 | 3.816 | 3.84 | 3.5
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 7.7 | 0.99907 | 3.4524 | 3.4557 | 3.4559 | 3.4499 | 3.4595 | 3.2 | 4
Morven | Morven | 132/66 | 30 |  |  | 0 | 0.99875 | 7.421 | 7.544 | 7.6327 | 7.7642 | 7.8354 | 0 | 4
Albury | Corowa | 132/22 | 30 | 27/30 |  | 33 | 0.99653 | 14.5628 | 14.4861 | 14.4919 | 14.552 | 14.5943 | 9.54 | 2
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 48.4 | 0.99763 | 37.0951 | 36.8758 | 36.6926 | 36.6847 | 36.5406 | 18.28 | 3.5
Albury | Mulwala | 132/22 | 30 | 30 |  | 33 | 0.9901 | 13.03 | 13.0576 | 13.0438 | 13.0865 | 13.1148 | 7.66 | 5.5
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 77 | 0.99387 | 51.9555 | 53.184 | 54.3025 | 55.5159 | 56.6334 | 49.84 | 3
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 33 | 1 | 12.111 | 12.1495 | 12.15 | 12.1859 | 12.2099 | 10.44 | 3
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.98732 | 3.0243 | 3.0232 | 3.0359 | 3.0389 | 3.045 | 2.34 | 7
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 11 | 0.99974 | 5.1992 | 5.2366 | 5.2918 | 5.3385 | 5.4019 | 4.37 | 2
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 33 | 0.99798 | 19.0961 | 19.2194 | 19.0835 | 19.1094 | 19.1248 | 12.7 | 6
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 5.5 | 0.99622 | 4.6123 | 4.6593 | 4.7141 | 4.7594 | 4.8112 | 2.36 | 3
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 33 | 0.9986 | 15.0183 | 15.2547 | 15.4647 | 15.6643 | 15.8376 | 9.39 | 3
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 5.5 | 0.99977 | 1.5653 | 1.5844 | 1.5742 | 1.5776 | 1.5654 | 1.1 | 5
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0.8678 | 0.61224 | 0.60989 | 0.60678 | 0.60315 | 0.6 | 0 | 3.5
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 27.5 | 0.95408 | 12.3111 | 12.2983 | 12.3503 | 12.3731 | 12.3952 | 0.41 | 3.5
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 8.25 | 0.9728 | 1.6965 | 1.6784 | 1.6646 | 1.6615 | 1.6567 | 0.87 | 3
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 13.75 | 0.87782 | 3.4328 | 3.416 | 3.4145 | 3.418 | 3.4184 | 1.31 | 3
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 2.75 | 0.91024 | 0.89272 | 0.88528 | 0.86032 | 0.84957 | 0.84135 | 0.11 | 5
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.77341 | 2.2459 | 2.2295 | 2.2134 | 2.2059 | 2.1915 | 0.51 | 11.5
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.65 | 0.91949 | 0.74038 | 0.72892 | 0.71594 | 0.70693 | 0.69991 | 0.24 | 4.5
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 33 | 0.9915 | 8.8578 | 8.8608 | 8.8501 | 8.8714 | 8.8959 | 1.1 | 12
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 11 | 0.99503 | 4.7963 | 4.8285 | 4.8727 | 4.9014 | 4.936 | 3.53 | 4
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 17.6 | 0.99986 | 11.6036 | 11.7825 | 11.8812 | 11.985 | 12.081 | 3.82 | 5
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.1 | 0.97593 | 0.94753 | 0.94396 | 0.9396 | 0.93717 | 0.93302 | 0.36 | 2.5
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 13.75 | 0.95605 | 11.31 | 11.5872 | 11.8911 | 12.1201 | 12.3778 | 6.32 | 4
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 55 | 0.99571 | 23.5403 | 23.5123 | 23.5301 | 23.5067 | 23.6067 | 11.81 | 2
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 27.5 | 0.98638 | 14.0423 | 14.0718 | 14.1092 | 14.1691 | 14.1633 | 2.18 | 9
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | 0.97958 | 1.9119 | 1.9204 | 1.9305 | 1.9356 | 1.9477 | 0.61 | 4
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.9993 | 13.6659 | 13.7261 | 13.7847 | 13.7914 | 13.893 | 8.28 | 3
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 2.75 | 0.91465 | 1.006 | 1.001 | 0.98847 | 0.97816 | 0.969 | 0.45 | 5.5
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0.89264 | 0.46404 | 0.46505 | 0.4705 | 0.46692 | 0.46776 | 0 | 3
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.94222 | 1.8932 | 1.9084 | 1.8987 | 1.9002 | 1.9071 | 0.36 | 2
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 10.45 | 0.99992 | 6.7085 | 6.7225 | 6.7213 | 6.7298 | 6.7282 | 2.18 | 4
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.95205 | 0.43035 | 0.43728 | 0.44399 | 0.45065 | 0.45819 | 0.15 | 3.5
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.97563 | 18.6569 | 18.6719 | 18.6465 | 18.5829 | 18.569 | 9.04 | 5
Yanco | Murrami | 33/11 | 5 | 5 |  | 5.5 | 0.83513 | 1.434 | 1.4407 | 1.4383 | 1.4428 | 1.4495 | 0.55 | 16
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.96675 | 10.251 | 10.2799 | 10.3421 | 10.4293 | 10.4953 | 5.72 | 3
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.98121 | 3.978 | 3.9578 | 3.9689 | 3.9437 | 3.8957 | 0.97 | 7
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.97651 | 2.5257 | 2.5361 | 2.5385 | 2.5475 | 2.5603 | 1.87 | 4
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.98306 | 10.33 | 10.3162 | 10.3133 | 10.3166 | 10.3109 | 1.13 | 3.5
Buronga | Powercor Robinvale 22kV Euston Distribution Supply | [5 empty] | 0.97818 | 6.2624 | 6.3117 | 6.3954 | 6.4339 | 6.4887 | 2.12 | 10
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply | [5 empty] | 0.99994 | 3.8343 | 3.8458 | 3.8541 | 3.8649 | 3.8836 | 1.33 | 2.5
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 33 | 0.98069 | 14.1033 | 14.0853 | 14.0589 | 14.0421 | 14.0416 | 6.46 | 2
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 33 | 0.99004 | 7.4141 | 7.2069 | 7.0376 | 6.9205 | 6.7311 | 4.75 | 3
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.99993 | 2.6659 | 2.6845 | 2.6696 | 2.6895 | 2.6662 | 0.91 | 4.5
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0.93146 | 6.6865 | 6.7006 | 6.737 | 6.7507 | 6.7473 | 0 | 49
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0.99776 | 0.2805 | 0.25406 | 0.28007 | 0.26961 | 0.2727 | 0 | 30

## ZSWinter
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (POE50 MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 2025 | 2026 | 2027 | 2028 | 2029
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 36 | 0.99373 | 13.291 | 13.4946 | 13.6774 | 13.8351 | 14.0364 | 16.76 | 5
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 36 | 0.99948 | 14.5393 | 14.629 | 14.7169 | 14.7829 | 14.9119 | 16.12 | 4
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 48 | 0.99807 | 11.8324 | 11.903 | 12.0669 | 12.2135 | 12.344 | 0 | 3.5
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 18 | 0.99794 | 12.0031 | 12.2108 | 12.4407 | 12.6739 | 12.9038 | 17.1 | 3.5
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99991 | 20.0158 | 20.0991 | 20.2289 | 20.3672 | 20.4504 | 23.91 | 5.5
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 240 | 0.99999 | 86.3743 | 87.1663 | 88.4008 | 89.4741 | 90.2272 | 0 | 3
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 36 | 0.99244 | 7.1714 | 7.3014 | 7.4933 | 7.6318 | 7.7811 | 10.61 | 3
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 30 | 0.99994 | 11.7121 | 11.7503 | 11.7932 | 11.8172 | 11.8481 | 5.48 | 6
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 36 | 0.99972 | 12.562 | 12.6188 | 12.6671 | 12.7576 | 12.8325 | 16.79 | 5
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 24 | 0.999 | 11.4193 | 11.3741 | 11.336 | 11.2956 | 11.2338 | 15.86 | 2
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 36 | 0.99712 | 28.3102 | 28.3321 | 28.2145 | 28.2782 | 28.2935 | 30.43 | 3
Lismore | Ballina 132kV | 132/66 | 75/112 |  |  | 0 | 0.99864 | 20.1128 | 20.1488 | 20.1072 | 20.1367 | 20.1843 | 0 | 3
Lismore | Dunoon | 132/11 | 10 | 10 |  | 12 | 0.99531 | 6.7036 | 6.7168 | 6.7319 | 6.7067 | 6.7305 | 8.05 | 4
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 54 | 0.99957 | 17.5707 | 17.5954 | 17.673 | 17.767 | 17.7944 | 19.45 | 5
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 12 | 0.99681 | 7.1174 | 7.1701 | 7.2401 | 7.3001 | 7.3458 | 7.4 | 3
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 19.2 | 0.99977 | 7.3036 | 7.3571 | 7.4252 | 7.5102 | 7.5987 | 8.18 | 2
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 288 | 0.99801 | 69.7499 | 69.6137 | 69.5668 | 69.6621 | 69.701 | 0 | 2
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 27.6 | 0.9995 | 13.8755 | 14.0419 | 14.298 | 14.5327 | 14.6956 | 16.38 | 2.5
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 57.6 | 0.99999 | 8.6019 | 8.5562 | 8.5181 | 8.5744 | 8.5728 | 7.42 | 3
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 36 | 0.99691 | 16.4375 | 16.7374 | 16.9491 | 17.2233 | 17.543 | 16.68 | 3
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 12 | 0.99859 | 9.3114 | 9.429 | 9.5704 | 9.7297 | 9.8879 | 11.56 | 4
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | 0.99855 | 13.1059 | 13.2642 | 13.4101 | 13.5668 | 13.7303 | 13.66 | 3
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 12 | 0.99826 | 7.0746 | 7.1163 | 7.1968 | 7.2569 | 7.3351 | 8.85 | 3
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 3 | 0.89761 | 0.77321 | 0.77171 | 0.7696 | 0.76804 | 0.76491 | 0.94 | 8
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0.99799 | 23.8425 | 24.1291 | 24.4269 | 24.8335 | 25.1498 | 0 | 2.5
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 36 | 0.99736 | 20.0446 | 20.2155 | 20.3393 | 20.5311 | 20.6556 | 18.79 | 3.5
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 4.2 | 0.99999 | 3.1429 | 3.2009 | 3.2583 | 3.3109 | 3.3711 | 0 | 7.5
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 3 | 0.99914 | 1.2625 | 1.27 | 1.2833 | 1.299 | 1.3013 | 0.97 | 4
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 6 | 0.99996 | 0.63331 | 0.66844 | 0.69819 | 0.72275 | 0.75735 | 0.7 | 1.5
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 3 | 0.99878 | 0.97078 | 0.98922 | 1.0087 | 1.0285 | 1.0451 | 0.76 | 7
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 30 | 0.99273 | 13.128 | 13.1661 | 13.2076 | 13.252 | 13.2856 | 12.6 | 4
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 29.4 | 0.99996 | 13.076 | 13.1073 | 13.14 | 13.1897 | 13.2694 | 13.79 | 3
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | 0.96886 | 2.587 | 2.6346 | 2.6801 | 2.7238 | 2.7748 | 2.82 | 1
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.70447 | 9.0179 | 9.0953 | 9.1167 | 9.0317 | 9.0234 | 11.73 | 7.5
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0.99862 | 0.33295 | 0.33208 | 0.33359 | 0.3331 | 0.33185 | 0 | 5.5
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.72 | 0.95537 | 0.28361 | 0.27922 | 0.27961 | 0.28381 | 0.29056 | 0.35 | 3
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.6 | 0.99853 | 0.33232 | 0.33166 | 0.33155 | 0.332 | 0.3327 | 0.26 | 5.5
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | 0.99928 | 1.1621 | 1.1854 | 1.2083 | 1.2358 | 1.2604 | 1.18 | 8
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 27.6 | 0.99375 | 10.5345 | 10.5084 | 10.4682 | 10.4624 | 10.4671 | 12.47 | 6
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 36 | 0.99685 | 10.542 | 10.6459 | 10.8616 | 10.9797 | 11.1242 | 9.84 | 3.5
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 36 | 0.98744 | 8.9369 | 8.9987 | 9.0416 | 9.1149 | 9.1855 | 0 | 3
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 55.2 | 0.99994 | 22.0435 | 22.2293 | 22.4283 | 22.6231 | 22.8264 | 18.1 | 4.5
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 36 | 0.99994 | 17.4209 | 17.5909 | 17.7334 | 17.9069 | 18.0684 | 12.72 | 6
Coffs Harbour | Dorrigo | 66/11, 132/11 | 7.5/10 | 10 |  | 12 | 0.99975 | 2.6766 | 2.6745 | 2.6801 | 2.6781 | 2.6853 | 2.82 | 4.5
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.99907 | 6.001 | 6.1907 | 6.3565 | 6.5299 | 6.7057 | 8.46 | 3
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 7.5 | 0.95296 | 2.881 | 2.9582 | 3.0419 | 3.1222 | 3.1953 | 3.22 | 7
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 29.4 | 0.90625 | 10.4235 | 10.5054 | 10.609 | 10.7446 | 10.8399 | 8.51 | 7
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.97954 | 0.49155 | 0.50124 | 0.51168 | 0.52317 | 0.53116 | 0.5 | 3.5
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 36 | 0.9929 | 12.8136 | 13.109 | 13.3625 | 13.6542 | 13.9335 | 14.97 | 3.5
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 36 | 0.99897 | 9.7069 | 9.7843 | 9.8399 | 9.9331 | 10.0051 | 10.88 | 5.5
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 27.6 | 0.99632 | 8.6867 | 8.7366 | 8.8113 | 8.8677 | 8.9121 | 8.88 | 4
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 36 | 0.99929 | 11.1081 | 11.1273 | 11.149 | 11.1197 | 11.1715 | 11.87 | 3
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.8 | 0.99641 | 1.9498 | 1.9608 | 1.9613 | 1.9613 | 1.966 | 1.72 | 1.5
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.6 | 0.99839 | 1.2702 | 1.3027 | 1.334 | 1.3748 | 1.4042 | 1.53 | 8.5
Kempsey | North St | 33/11 | 10 | 16 |  | 12 | 0.99848 | 10.4934 | 10.6073 | 10.73 | 10.8488 | 10.9638 | 8.02 | 7
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 18 | 0.99992 | 7.8563 | 7.8432 | 7.8456 | 7.8861 | 7.8662 | 7.06 | 9
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 6 | 0.99526 | 4.0771 | 4.1656 | 4.2452 | 4.3275 | 4.4119 | 2.76 | 4.5
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 15 | 0.99612 | 7.5307 | 7.6726 | 7.7929 | 7.9619 | 8.0836 | 7.66 | 1.5
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 36 | 0.99681 | 18.2243 | 18.3146 | 18.5166 | 18.5458 | 18.7236 | 13.88 | 3.5
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.6 | 0.99432 | 1.3431 | 1.3533 | 1.3571 | 1.368 | 1.3809 | 1.33 | 2
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 36 | 0.99824 | 22.9979 | 23.4636 | 23.7842 | 24.2048 | 24.8054 | 26.78 | 2.5
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 4.2 | 0.99971 | 2.1943 | 2.2687 | 2.3461 | 2.4274 | 2.5074 | 2.91 | 2
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 9.6 | 0.99841 | 6.8333 | 7.1094 | 7.3691 | 7.6574 | 7.9236 | 9.13 | 2
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 24 | 0.99041 | 16.1688 | 16.1891 | 16.1877 | 16.1931 | 16.1798 | 7.41 | 3.5
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 18 | 0.99994 | 11.8346 | 12.2112 | 12.6083 | 12.9859 | 13.318 | 12.6 | 2
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.8 | 0.99763 | 1.779 | 1.833 | 1.8888 | 1.9428 | 1.9962 | 2.08 | 5
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0.99933 | 12.4668 | 12.8074 | 13.1851 | 13.538 | 13.8858 | 0 | 2
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | 0.96545 | 1.0006 | 0.99793 | 0.99618 | 0.99047 | 0.98982 | 1.01 | 5
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.8 | 0.99892 | 3.8791 | 3.9416 | 3.9917 | 4.0718 | 4.1452 | 4.9 | 1.5
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 24 | 0.99972 | 8.6353 | 8.6713 | 8.7598 | 8.8005 | 8.9021 | 8.61 | 2
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 8.4 | 0.99927 | 7.0265 | 7.1788 | 7.3288 | 7.4635 | 7.6232 | 7.63 | 2
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 6 | 0.99725 | 3.9782 | 3.9825 | 3.9852 | 3.9848 | 3.9884 | 1.78 | 1.5
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 0.99978 | 2.5773 | 2.6194 | 2.681 | 2.7408 | 2.7975 | 2.8 | 3
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99802 | 16.534 | 16.7218 | 16.8938 | 17.0844 | 17.2867 | 13.91 | 2.5
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 19.2 | 0.99615 | 8.2964 | 8.3294 | 8.3449 | 8.3347 | 8.4002 | 9.98 | 4
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 7.5 | 0.99943 | 3.6767 | 3.7834 | 3.906 | 4.0113 | 4.1124 | 4.83 | 3
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 30 | 0.9895 | 11.3942 | 11.4846 | 11.5727 | 11.6084 | 11.7122 | 8.6 | 12
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 19.2 | 0.99975 | 7.2238 | 7.2453 | 7.2498 | 7.3218 | 7.3336 | 4.89 | 4.5
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 24 | 0.99906 | 15.051 | 15.0788 | 15.0508 | 15.0956 | 15.0864 | 10.33 | 7
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 12 | 0.99609 | 8.6297 | 8.7761 | 8.9715 | 9.1458 | 9.2966 | 8.01 | 8
Stroud | Booral | 33/11 | 3 | 2.5 |  | 3 | 0.95277 | 1.1486 | 1.1502 | 1.1521 | 1.151 | 1.1559 | 1.24 | 6
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 0.9911 | 3.2476 | 3.3146 | 3.3832 | 3.4491 | 3.5183 | 2.82 | 9
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99886 | 6.098 | 6.1403 | 6.166 | 6.1963 | 6.2178 | 5.94 | 5.5
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99637 | 7.3672 | 7.3807 | 7.4037 | 7.4135 | 7.4435 | 6.76 | 8
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 0.99463 | 1.723 | 1.7493 | 1.7764 | 1.8041 | 1.8386 | 1.69 | 5
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 9.6 | 0.99997 | 2.4047 | 2.443 | 2.4715 | 2.517 | 2.5393 | 2.81 | 9
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 9.6 | 0.9997 | 4.7712 | 4.8142 | 4.8635 | 4.9563 | 4.9943 | 3.95 | 2.5
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 72 | 0.99649 | 38.6318 | 38.9933 | 39.7043 | 40.1351 | 40.8014 | 0.01 | 5
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 6 | 0.99999 | 2.1814 | 2.1799 | 2.1708 | 2.1745 | 2.1735 | 2.08 | 4
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0.99903 | 8.4909 | 8.5919 | 8.6862 | 8.8432 | 8.9165 | 0 | 4
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99983 | 7.7563 | 7.7936 | 7.847 | 7.8798 | 7.8807 | 7.63 | 5
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply | [5 empty] | 0.99756 | 5.7082 | 5.7696 | 5.7999 | 5.8681 | 5.9323 | 2.74 | 11
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 3 | 0.99922 | 2.2162 | 2.258 | 2.2954 | 2.3337 | 2.3798 | 1.9 | 6
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 15 | 0.99954 | 13.7198 | 13.9015 | 14.0633 | 14.1905 | 14.3635 | 9.46 | 4
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.98299 | 0.46672 | 0.4908 | 0.51199 | 0.51421 | 0.53776 | 0.22 | 5.5
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 15 | 0.99447 | 12.2798 | 12.5387 | 12.8279 | 13.1091 | 13.3866 | 6.32 | 5
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 19.2 | 0.99972 | 10.0972 | 10.1336 | 10.1389 | 10.1701 | 10.1959 | 6.1 | 4
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 4.2 | 0.94501 | 0.45349 | 0.45417 | 0.45566 | 0.45706 | 0.45776 | 0.23 | 7
Armidale | Uralla | 66/11 | 8 | 5 |  | 6 | 0.95697 | 3.8419 | 3.8562 | 3.885 | 3.9015 | 3.9213 | 3.57 | 6
Armidale | Walcha South 66/22kV | 66/22 | 8 | 8/10 |  | 9.6 | 0.74544 | 2.3529 | 2.376 | 2.3961 | 2.4188 | 2.4297 | 1.06 | 5.5
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.6 | 0.99993 | 1.7116 | 1.7478 | 1.7779 | 1.8187 | 1.8454 | 1.24 | 12
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.95325 | 0.97488 | 0.99062 | 1.002 | 1.0152 | 1.0279 | 1.29 | 2
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | 0.78477 | 0.16122 | 0.16187 | 0.16131 | 0.16159 | 0.16221 | 0.13 | 2
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 24 | 0.99983 | 8.9848 | 9.0448 | 9.1109 | 9.1901 | 9.2461 | 6.95 | 4
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 6 | 0.99959 | 4.5852 | 4.641 | 4.6892 | 4.7476 | 4.8022 | 3.36 | 9
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0.99999 | 0.0012393 | 0.0010999 | 0.0011779 | 0.0013402 | 0.0010978 | 0.01 | 0
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.95225 | 0.60543 | 0.61142 | 0.61488 | 0.62094 | 0.62485 | 0.84 | 7
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.6 | 0.97806 | 2.2837 | 2.3316 | 2.3837 | 2.4441 | 2.4914 | 2.2 | 3.5
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 36 | 0.99992 | 21.0552 | 21.2409 | 21.2934 | 21.4069 | 21.5749 | 16 | 4
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | 0.66412 | 1.3577 | 1.3667 | 1.3759 | 1.3855 | 1.3923 | 0.77 | 5
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.8 | 0.95184 | 0.94186 | 0.94411 | 0.94481 | 0.94299 | 0.94594 | 0 | 1.5
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 6 | 0.95231 | 2.4285 | 2.449 | 2.4779 | 2.4934 | 2.5158 | 1.51 | 2
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 6 | 0.95085 | 1.8593 | 1.9011 | 1.9485 | 1.9913 | 2.0357 | 0.61 | 1.5
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | 0.89002 | 0.21367 | 0.21507 | 0.21729 | 0.21882 | 0.22055 | 0.13 | 2
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.8 | 0.96672 | 2.9127 | 2.9553 | 3.0015 | 3.0532 | 3.0953 | 2.39 | 4.5
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.9511 | 1.7852 | 1.7869 | 1.7927 | 1.7926 | 1.793 | 0.94 | 5
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 18 | 0.99898 | 17.4782 | 17.4859 | 17.5033 | 17.5375 | 17.4961 | 7.04 | 3
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.98655 | 5.427 | 5.5655 | 5.704 | 5.845 | 5.987 | 2.92 | 15
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.99456 | 3.8626 | 3.8508 | 3.8336 | 3.8981 | 3.7793 | 0.55 | 15
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 3 | 0.99513 | 0.92806 | 0.94553 | 0.95689 | 0.97218 | 0.98711 | 0.56 | 4
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 36 | 0.99871 | 22.7221 | 22.9438 | 24.9845 | 29.5645 | 33.8201 | 14.26 | 14
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.95214 | 5.702 | 5.7102 | 5.7064 | 5.7058 | 5.7076 | 1.29 | 15.5
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.95595 | 6.4004 | 6.3849 | 6.3827 | 6.3949 | 6.3565 | 0.23 | 8
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | 0.93306 | 3.0115 | 3.0109 | 3.0343 | 3.0545 | 3.0639 | 0.09 | 35
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.91654 | 2.4342 | 2.4505 | 2.477 | 2.4963 | 2.5205 | 1.28 | 3
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 6 | 0.99525 | 1.6462 | 1.6472 | 1.6492 | 1.654 | 1.6488 | 0.76 | 4
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 6 | 0.99543 | 3.1544 | 3.1792 | 3.2098 | 3.2264 | 3.2544 | 2.57 | 4
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0.99651 | 2.5602 | 2.5609 | 2.5574 | 2.562 | 2.5537 | 0.7 | 27.5
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 36 | 0.99511 | 17.377 | 17.3866 | 17.4205 | 17.3453 | 17.3645 | 10.71 | 7
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 12 | 0.95552 | 5.3004 | 5.4091 | 5.5488 | 5.6672 | 5.8093 | 3.26 | 2.5
Narrabri | Wee Waa | 66/22 | 10 | 16 |  | 12 | 0.97589 | 10.2738 | 10.4806 | 10.5685 | 10.7054 | 10.8681 | 3.15 | 10.5
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.8 | 0.99666 | 4.9419 | 5.0096 | 5.0731 | 5.1676 | 5.2531 | 1.83 | 8
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 36 | 0.98092 | 23.7441 | 24.0498 | 24.3979 | 24.8345 | 25.2314 | 13.31 | 4
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0.98818 | 0.19543 | 0.19968 | 0.20394 | 0.20856 | 0.21275 | 0.03 | 2
Tamworth | Attunga | 66/11 | 5 | 8 |  | 6 | 0.95097 | 2.3574 | 2.3591 | 2.3628 | 2.364 | 2.3642 | 1.77 | 7
Tamworth | Barraba | 66/11 | 5 | 5 |  | 6 | 0.99994 | 2.3116 | 2.3252 | 2.335 | 2.3519 | 2.3627 | 2.12 | 9
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.2 | 0.99869 | 0.73563 | 0.73979 | 0.74337 | 0.74645 | 0.75015 | 0.64 | 6
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.4 | 0.95497 | 0.67723 | 0.68055 | 0.68456 | 0.68757 | 0.69108 | 0.15 | 2
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.8 | 0.9774 | 0.97465 | 0.97645 | 0.97595 | 0.97521 | 0.97529 | 0.42 | 5
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.95227 | 1.0876 | 1.101 | 1.1141 | 1.1279 | 1.1416 | 0.6 | 6
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 36 | 0.99402 | 10.6736 | 17.9555 | 19.2512 | 21.2455 | 22.9729 | 4.26 | 15.5
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.99792 | 5.7441 | 5.8309 | 5.9336 | 6.0493 | 6.1602 | 4.75 | 5
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 7.5 | 0.90359 | 3.8449 | 3.8747 | 3.9073 | 3.9291 | 3.9549 | 3.21 | 4
Tamworth | Murrurundi | 33/11 | 5/8 | 5/8 |  | 9.6 | 0.99969 | 2.5873 | 2.6343 | 2.6825 | 2.7305 | 2.7793 | 2.04 | 6.5
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 3 | 0.9559 | 1.6908 | 1.711 | 1.7345 | 1.7629 | 1.7878 | 1.28 | 2
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 36 | 0.99354 | 19.0733 | 19.4681 | 19.8085 | 20.2031 | 20.5599 | 13.56 | 6
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 15.96 | 0.99948 | 6.0987 | 6.2275 | 6.3767 | 6.5341 | 6.6621 | 4.71 | 4
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 12 | 0.99976 | 4.4633 | 4.5499 | 4.6241 | 4.7027 | 4.7924 | 0 | 5
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.98313 | 0.64494 | 0.64753 | 0.64918 | 0.65055 | 0.65166 | 0.19 | 5
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 55.2 | 0.99942 | 26.9805 | 27.0883 | 27.0982 | 27.2379 | 27.255 | 14.27 | 4
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 36 | 0.9988 | 23.4328 | 23.5937 | 23.7295 | 23.939 | 24.0691 | 14.99 | 3.5
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.97979 | 0.50001 | 0.50007 | 0.49748 | 0.49502 | 0.49448 | 0.12 | 1.5
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 7.5 | 0.94853 | 2.3343 | 2.3288 | 2.3283 | 2.327 | 2.326 | 1.45 | 4.5
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 15.6 | 0.99303 | 8.6343 | 8.7078 | 8.7985 | 8.876 | 8.9655 | 6.88 | 5
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 12 | 0.98509 | 5.5242 | 5.6036 | 5.6686 | 5.7501 | 5.8425 | 4.26 | 8
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | 0.99928 | 3.4718 | 3.4538 | 3.476 | 3.4723 | 3.4896 | 2.38 | 7
Beryl | Mudgee | 66/22, 132/22 | 18/30 | 30 |  | 36 | 0.99788 | 24.66 | 25.0848 | 25.5161 | 26.0648 | 26.437 | 18.48 | 11
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 3 | 0.95421 | 3.088 | 3.1868 | 3.2775 | 3.3377 | 3.4298 | 1.67 | 1
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 3 | 0.95358 | 1.1216 | 1.1224 | 1.1237 | 1.1235 | 1.1195 | 0.89 | 12.5
Wellington | Wellington 11kV | 132/11, 66/11 | 10 | 15 |  | 12 | 0.99776 | 9.1141 | 9.2419 | 9.3398 | 9.4103 | 9.5305 | 5.49 | 4.5
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 12 | 0.97726 | 5.3856 | 5.4172 | 5.4482 | 5.4864 | 5.5212 | 3.61 | 10.5
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 108 | 0.9978 | 53.7437 | 54.0836 | 54.6132 | 55.0348 | 55.2488 | 0 | 7.5
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 36 | 0.97856 | 17.8819 | 17.8417 | 17.8273 | 17.7171 | 17.6994 | 7.27 | 9
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 36 | 0.99982 | 17.4225 | 17.5858 | 17.6877 | 17.7605 | 17.9197 | 15.49 | 3
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 27.6 | 0.99918 | 14.1221 | 14.1898 | 14.2828 | 14.3423 | 14.4469 | 12.29 | 6
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 36 | 0.99998 | 17.4672 | 17.4985 | 17.519 | 17.5293 | 17.5582 | 17.92 | 6
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | 0.99857 | 1.2281 | 1.2257 | 1.2306 | 1.2333 | 1.2351 | 1.21 | 6.5
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 14.4 | 0.99949 | 6.361 | 6.4029 | 6.4508 | 6.4994 | 6.5403 | 4.82 | 7.5
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.9514 | 1.5295 | 1.524 | 1.5179 | 1.5138 | 1.5092 | 1.01 | 6
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 28.8 | 0.99998 | 12.6799 | 12.7908 | 12.9403 | 13.1022 | 13.1275 | 8.35 | 6.5
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 12 | 0.99667 | 8.3338 | 8.3794 | 8.3693 | 8.3554 | 8.3557 | 3.64 | 8
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 30 | 0.97102 | 6.9307 | 6.9301 | 6.953 | 6.9485 | 6.9572 | 2.15 | 19
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 12 | 0.99743 | 6.2581 | 6.2537 | 6.2725 | 6.3551 | 6.3031 | 2.54 | 4
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.60744 | 2.8236 | 2.8225 | 2.8223 | 2.8267 | 2.8329 | 0.79 | 1.5
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.2 | 0.97828 | 0.080336 | 0.080741 | 0.081023 | 0.081327 | 0.081537 | 0.04 | 1
Nyngan | Cobar CSA | 132/11 | 15/18 |  |  | 0 | 0.99033 | 17.982 | 18.0331 | 18.0887 | 18.1618 | 18.2125 | 0 | 6.5
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 18 | 0.91415 | 1.9189 | 1.9351 | 1.9176 | 1.8513 | 1.7948 | 0 | 14
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 24 | 0.95179 | 11.2606 | 11.3854 | 11.4355 | 11.5629 | 11.6868 | 0 | 142
Nyngan | Cobar Town | 66/22 | 8/11 | 10/13 |  | 13.2 | 0.9522 | 5.8562 | 5.861 | 5.8591 | 5.8646 | 5.8724 | 5.25 | 6
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0.91477 | 3.2416 | 3.3127 | 3.3617 | 3.4192 | 3.4601 | 0 | 8
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 36 | 0.9999 | 29.2885 | 29.4012 | 29.5771 | 29.5971 | 29.7312 | 0 | 10
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 12 | 0.99136 | 7.1204 | 7.264 | 7.4142 | 7.5734 | 7.7356 | 2.91 | 7
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply | [5 empty] | 0.99975 | 36.0444 | 38.3299 | 38.351 | 38.4261 | 38.3752 | 25.4 | 15
Broken Hill | Wilcannia 33kV | [5 empty] | 0.80864 | 0.57976 | 0.588 | 0.59662 | 0.60387 | 0.61174 | 0.36 | 8.5
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 6 | 0.99644 | 0.71256 | 0.71336 | 0.71692 | 0.71775 | 0.71906 | 1.06 | 6
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.8 | 0.76105 | 1.2364 | 1.2906 | 1.3413 | 1.3919 | 1.4434 | 0.93 | 12.5
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.8 | 0.96211 | 0.47513 | 0.47487 | 0.45932 | 0.4644 | 0.46671 | 0.21 | 28
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 18 | 0.83289 | 5.6948 | 6.3532 | 6.4169 | 6.4745 | 6.5347 | 0 | 15
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | 0.94372 | 0.66663 | 0.67029 | 0.67676 | 0.6807 | 0.68745 | 0.37 | 1
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.8 | 0.96789 | 1.9515 | 1.985 | 2.0376 | 2.0956 | 2.1578 | 0.24 | 10
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 4.2 | 0.99363 | 0.95743 | 0.97368 | 0.99078 | 1.0074 | 1.0221 | 0.67 | 4
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 12 | 0.99968 | 12.2272 | 12.3424 | 12.5139 | 12.6219 | 12.7695 | 12.01 | 5.5
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 36 | 0.93891 | 16.1248 | 16.1254 | 16.138 | 16.0607 | 16.0796 | 8.27 | 8
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 36 | 0.99762 | 23.5113 | 23.7626 | 24.0144 | 24.2687 | 24.5734 | 13.83 | 10
Orange | Orange West | 66/11 | 30 | 30 |  | 36 | 1 | 14.7459 | 14.8442 | 14.993 | 15.0771 | 15.3123 | 12.21 | 8
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 3 | 0.95503 | 1.8678 | 1.9214 | 1.9799 | 2.0226 | 2.0667 | 1.57 | 3
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 28.8 | 0.97882 | 9.5582 | 9.5403 | 9.5213 | 9.5239 | 9.5075 | 2.12 | 19
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.8 | 0.99773 | 3.5839 | 3.6056 | 3.6246 | 3.6478 | 3.6691 | 2.89 | 3
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 24 | 0.99081 | 12.7214 | 12.8741 | 12.9413 | 13.0365 | 13.0979 | 5.62 | 5.5
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 3 | 0.99941 | 2.5042 | 2.518 | 2.5298 | 2.5408 | 2.5556 | 1.94 | 4
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 36 | 0.99937 | 21.192 | 21.3373 | 21.4196 | 21.5544 | 21.6675 | 13.13 | 8
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 72 | 0.99677 | 25.0953 | 25.0845 | 25.0459 | 25.0927 | 25.082 | 11.93 | 4
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 24 | 0.99893 | 20.6534 | 20.9725 | 21.2134 | 21.4808 | 21.7679 | 15.17 | 4
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0.84798 | 0.5195 | 0.51899 | 0.52093 | 0.52235 | 0.52354 | 0 | 1.5
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 54 | 0.90992 | 34.7506 | 35.4008 | 36.18 | 36.8098 | 37.7263 | 0 | 32.5
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 18 | 0.99998 | 5.8898 | 5.9098 | 5.9136 | 5.9424 | 5.9599 | 4.23 | 10
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 36 | 0.99921 | 17.334 | 17.5874 | 17.7948 | 18.0817 | 18.2703 | 12.99 | 3
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 12 | 0.99981 | 1.4779 | 1.4778 | 1.4815 | 1.4811 | 1.4827 | 1.68 | 3.5
Parkes | Trundle | 66/22 | 8 | 5 |  | 6 | 0.99386 | 3.1475 | 3.1502 | 3.1584 | 3.2326 | 3.2546 | 2.36 | 7
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 12 | 0.99592 | 7.0686 | 7.1312 | 7.1888 | 7.287 | 7.333 | 5.31 | 4
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 36 | 0.99588 | 11.5559 | 11.5832 | 11.5885 | 11.5992 | 11.6306 | 9.14 | 6
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 8.4 | 0.98856 | 3.4096 | 3.4211 | 3.4221 | 3.4292 | 3.4269 | 3.19 | 2
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 6 | 0.9432 | 4.2093 | 4.2043 | 4.2151 | 4.2273 | 4.2532 | 1.34 | 4
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.8 | 0.99965 | 1.4977 | 1.4995 | 1.4949 | 1.5062 | 1.5045 | 0.45 | 1.5
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 54 | 0.99906 | 20.7621 | 20.9104 | 21.0199 | 21.1583 | 21.2573 | 14.07 | 8.5
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.6 | 0.99983 | 1.443 | 1.4502 | 1.4613 | 1.4637 | 1.4778 | 1.35 | 4.5
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 48 | 0.99707 | 35.5783 | 35.7967 | 36.1534 | 36.5413 | 36.9535 | 0 | 1.5
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99998 | 7.7551 | 7.8543 | 7.9496 | 8.0734 | 8.1801 | 6.43 | 5
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 15 | 0.99467 | 9.0704 | 9.1728 | 9.2259 | 9.3598 | 9.4308 | 8.25 | 5.5
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 15 | 1 | 8.3546 | 8.4206 | 8.512 | 8.5733 | 8.6374 | 6 | 5
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | 0.99956 | 2.7584 | 2.8094 | 2.845 | 2.908 | 2.9542 | 2.8 | 4
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 6 | 0.99506 | 1.3684 | 1.372 | 1.367 | 1.37 | 1.3675 | 0.72 | 5
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 6 | 0.96383 | 0.26578 | 0.26043 | 0.26525 | 0.27543 | 0.26628 | 0 | 25
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 24 | 0.99896 | 13.9459 | 14.1181 | 14.3152 | 14.4832 | 14.6919 | 7.22 | 9.5
Cooma | Eucumbene | 66/11 | 0.6 |  |  | 0 | 0.9605 | 0.24086 | 0.24428 | 0.24818 | 0.25295 | 0.25667 | 0.08 | 3
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 36 | 0.99932 | 12.2603 | 12.4409 | 12.5637 | 12.7386 | 12.8599 | 3.98 | 7
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0.9972 | 0.72739 | 0.72595 | 0.72788 | 0.72661 | 0.72581 | 0.26 | 2
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 12 | 0.99741 | 5.1117 | 5.2174 | 5.3123 | 5.4311 | 5.5539 | 2.84 | 5.5
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 1 | 0.18469 | 0.18324 | 0.18448 | 0.18241 | 0.18371 | 0 | 1
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.87342 | 5.31 | 5.3408 | 5.3024 | 5.3125 | 5.2785 | 0 | 14
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 1 | 1.2335 | 1.2705 | 1.3 | 1.3452 | 1.3841 | 0.2 | 4
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 0.99709 | 0.95101 | 0.95012 | 0.94693 | 0.94739 | 0.9473 | 0 | 3
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 12 | 0.95792 | 9.18 | 9.2281 | 9.3094 | 9.3852 | 9.4281 | 0.12 | 3.5
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0.91062 | 0.027805 | 0.028485 | 0.02819 | 0.028725 | 0.02861 | 0 | 5
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0.999 | 8.2846 | 8.2399 | 8.1897 | 8.2941 | 8.2213 | 0 | 6
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.96437 | 13.606 | 13.6256 | 13.6206 | 13.5866 | 13.5709 | 0.03 | 14
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.9998 | 45.205 | 46.1672 | 47.2731 | 48.306 | 49.5242 | 0 | 8.5
Bega | Bermagui | 33/11 | 5 | 5 |  | 6 | 0.99981 | 3.4477 | 3.4881 | 3.5511 | 3.6009 | 3.6623 | 3.14 | 7
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0.97788 | 0.76111 | 0.78065 | 0.79503 | 0.80991 | 0.83047 | 0.57 | 3
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 3 | 0.99899 | 1.7314 | 1.7584 | 1.7814 | 1.8213 | 1.8371 | 1.97 | 4
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.99932 | 4.8464 | 4.9347 | 5.0158 | 5.1132 | 5.1948 | 3.47 | 13
Bega | Edrom | 66/11 | 5 | 5 |  | 6 | 0.91924 | 2.2695 | 2.2649 | 2.2537 | 2.2504 | 2.2426 | 0 | 3.5
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0.99644 | 6.2594 | 6.4581 | 6.6706 | 6.8537 | 7.0725 | 0 | 6
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 36 | 0.99631 | 16.4185 | 16.6306 | 16.8573 | 17.0434 | 17.2731 | 10.39 | 8
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 19.2 | 0.99953 | 17.2216 | 17.3314 | 17.4686 | 17.5706 | 17.6743 | 12.92 | 7.5
Bega | Quira | 66/11 | 5 |  |  | 0 | 0.97746 | 1.5659 | 1.5597 | 1.5558 | 1.5544 | 1.5635 | 1.16 | 3
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 15.6 | 0.99718 | 5.0424 | 5.0964 | 5.1446 | 5.196 | 5.248 | 1.55 | 12
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | 0.99781 | 5.6327 | 5.6803 | 5.727 | 5.7843 | 5.8354 | 0 | 3.5
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.97736 | 0.90839 | 0.92854 | 0.94519 | 0.96536 | 0.98387 | 0.49 | 17
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 3 | 0.99962 | 1.3053 | 1.3049 | 1.3091 | 1.3095 | 1.3134 | 1.46 | 8
Tumut | Batlow | 66/11 | 5 | 5 |  | 6 | 0.98862 | 2.1242 | 2.1207 | 2.1122 | 2.1142 | 2.109 | 1.34 | 4
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 9.6 | 0.99988 | 5.7932 | 5.8489 | 5.9059 | 5.9531 | 6.0243 | 3.86 | 6
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.2 | 0.99591 | 0.83595 | 0.84594 | 0.85256 | 0.86652 | 0.87875 | 0.55 | 1.5
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.99512 | 0.098527 | 0.098255 | 0.09782 | 0.097422 | 0.096699 | 0.08 | 4
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | 0.78188 | 0.62069 | 0.63396 | 0.65564 | 0.67534 | 0.68408 | 0.36 | 2
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 9.6 | 0.99879 | 8.5125 | 8.5157 | 8.5191 | 8.5098 | 8.5173 | 3.34 | 6
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 36 | 0.99494 | 13.8663 | 13.8128 | 13.9315 | 13.8765 | 13.8883 | 7.62 | 3
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 12 | 0.99846 | 9.916 | 10.0498 | 10.2074 | 10.3212 | 10.484 | 9.5 | 8
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 6 | 0.99997 | 8.1291 | 8.5523 | 8.8725 | 9.2577 | 9.5321 | 3.57 | 8
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 12 | 0.99751 | 0.90088 | 0.91151 | 0.90878 | 0.91458 | 0.93168 | 0 | 2
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 36 | 0.99998 | 13.071 | 13.6692 | 14.2212 | 14.8176 | 15.3888 | 13.42 | 4.5
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 36 | 0.99658 | 18.8348 | 18.8716 | 18.9424 | 19.0257 | 19.1098 | 9.56 | 4
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 36 | 0.9993 | 22.6167 | 22.7848 | 23.0059 | 23.1308 | 23.2854 | 19.66 | 5
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 9.6 | 0.99253 | 5.2612 | 5.4235 | 5.5958 | 5.7492 | 5.9217 | 4.79 | 8
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 3 | 0.96307 | 2.6592 | 2.6762 | 2.6962 | 2.7133 | 2.7315 | 2.62 | 2.5
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 22.8 | 0.99133 | 16.0382 | 16.2278 | 16.4407 | 16.6563 | 16.9195 | 8.87 | 12
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 12 | 0.99997 | 4.346 | 4.3422 | 4.3248 | 4.3353 | 4.3492 | 4.61 | 8
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 36 | 0.99995 | 9.6816 | 9.7307 | 9.7767 | 9.8479 | 9.8575 | 4.72 | 11
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.99562 | 44.6861 | 44.9854 | 45.1832 | 45.814 | 46.0846 | 0 | 4
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 18 | 1 | 11.5807 | 11.5918 | 11.5942 | 11.6644 | 11.6457 | 8.54 | 2.5
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 18 | 0.99303 | 7.1237 | 7.3112 | 7.4832 | 7.6617 | 7.8329 | 3.01 | 9
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.94943 | 7.6624 | 7.7208 | 7.7813 | 7.8356 | 7.912 | 0 | 4
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 16.8 | 0.98942 | 7.2281 | 7.2278 | 7.2719 | 7.3413 | 7.3424 | 1.42 | 5
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | 0.99802 | 1.538 | 1.5444 | 1.5502 | 1.548 | 1.5553 | 1.44 | 6.5
Cowra | Canowindra | 66/11 | 5 | 8 |  | 6 | 0.99489 | 5.0165 | 5.0651 | 5.1092 | 5.1531 | 5.2017 | 3.88 | 3
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 36 | 0.99052 | 15.9612 | 16.0945 | 16.2313 | 16.371 | 16.5354 | 12.74 | 8.5
Cowra | Grenfell | 66/11 | 8 | 5 |  | 6 | 0.95608 | 4.7513 | 4.8023 | 4.8748 | 4.9334 | 5.028 | 4.22 | 6
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.99637 | 0.91892 | 0.92238 | 0.92655 | 0.93216 | 0.93725 | 0.68 | 3
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 6 | 0.99083 | 4.0214 | 4.1585 | 4.2933 | 4.442 | 4.5641 | 3.09 | 12
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 22.8 | 0.99914 | 8.7106 | 8.7848 | 8.8501 | 8.9249 | 9.0017 | 7.8 | 5.5
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.8 | 0.98107 | 1.4802 | 1.4696 | 1.4613 | 1.4506 | 1.439 | 0.43 | 6
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 12 | 0.99943 | 4.8747 | 4.9071 | 4.9584 | 4.99 | 5.0329 | 3.94 | 3.5
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 36 | 0.9962 | 18.0718 | 18.2802 | 18.5433 | 18.7371 | 18.9913 | 10.62 | 6
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 3 | 0.99974 | 1.3301 | 1.3802 | 1.4248 | 1.4752 | 1.5242 | 1.31 | 3.5
Yass | Marilba | 66/11 | 3 |  |  | 0 | 0.99989 | 1.6284 | 1.6447 | 1.6677 | 1.6944 | 1.7117 | 1.3 | 6
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | 0.99827 | 7.9828 | 8.1152 | 8.2641 | 8.4274 | 8.5582 | 8.78 | 9
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 15.6 | 0.9831 | 14.781 | 14.9088 | 14.9653 | 15.0888 | 15.198 | 10 | 5
Temora | Anona | 66/22 | 3 | 2.5 |  | 3 | 0.94507 | 1.1656 | 1.1735 | 1.1775 | 1.1839 | 1.187 | 0.99 | 8
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 3 | 0.99932 | 0.70961 | 0.71562 | 0.72026 | 0.72975 | 0.73251 | 0.64 | 1
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.6 | 0.99849 | 0.93406 | 0.94882 | 0.96335 | 0.9783 | 0.99479 | 0.74 | 4
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | 0.99984 | 0.21398 | 0.21562 | 0.21774 | 0.22028 | 0.22175 | 0.17 | 2
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.97175 | 16.7387 | 16.8943 | 17.1354 | 17.2141 | 17.4773 | 0 | 9
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 12 | 0.9998 | 6.9924 | 7.0776 | 7.1475 | 7.2364 | 7.3223 | 6.3 | 4.5
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 12 | 0.98432 | 7.5321 | 7.6369 | 7.7559 | 7.8642 | 7.9807 | 5.63 | 8.5
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.6 | 0.99748 | 0.69351 | 0.69666 | 0.70101 | 0.70494 | 0.7068 | 0.29 | 18
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 36 | 0.99938 | 10.2591 | 10.2438 | 12.5981 | 14.9528 | 17.3048 | 0.3 | 73
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/10 | 6.75/10 |  | 12 | 0.99907 | 8.5625 | 8.8607 | 9.1074 | 9.3905 | 9.6874 | 5.49 | 2
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.8 | 0.99212 | 1.3596 | 1.3623 | 1.3619 | 1.3627 | 1.3679 | 0 | 3
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 9.6 | 0.9998 | 4.2993 | 4.3458 | 4.3793 | 4.4257 | 4.4532 | 4.35 | 6
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.6 | 0.99068 | 0.87458 | 0.87021 | 0.87242 | 0.87171 | 0.86812 | 0.85 | 4.5
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 16.8 | 0.98996 | 4.9042 | 4.8901 | 4.8681 | 4.9032 | 4.8601 | 2.75 | 3.5
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | 0.99958 | 0.45466 | 0.45242 | 0.45051 | 0.45142 | 0.45129 | 0.24 | 2
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 18 | 0.99945 | 6.8001 | 6.8981 | 6.992 | 7.0831 | 7.1666 | 4.07 | 11
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | 0.99996 | 12.0454 | 12.0669 | 12.0948 | 12.1164 | 12.1682 | 0 | 6.5
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.99498 | 0.37438 | 0.36994 | 0.36509 | 0.35972 | 0.3577 | 0.39 | 4
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.4 | 0.99677 | 1.3487 | 1.3505 | 1.3492 | 1.3478 | 1.348 | 0 | 3
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 8.28 | 0.99699 | 3.2731 | 3.2965 | 3.313 | 3.3256 | 3.3508 | 0.59 | 3.5
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.2 | 0.90079 | 1.0173 | 1.0192 | 1.0203 | 1.0243 | 1.0281 | 0.81 | 2
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 36 | 0.99427 | 18.1327 | 18.2597 | 18.4238 | 18.5251 | 18.6751 | 11.61 | 4
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 15.96 | 0.99998 | 11.0619 | 11.1867 | 11.2849 | 11.393 | 11.5294 | 10.29 | 5.5
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0.96934 | 0.14665 | 0.14754 | 0.14837 | 0.14862 | 0.14692 | 0 | 3
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 36 | 0.9999 | 15.7075 | 15.973 | 16.2571 | 16.5616 | 16.8598 | 5.1 | 3
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 6 | 0.99999 | 2.2949 | 2.293 | 2.2924 | 2.2933 | 2.3029 | 2.12 | 4
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 30 | 0.99803 | 15.8122 | 15.9469 | 15.9644 | 16.0226 | 16.025 | 13.19 | 5
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 6 | 0.95387 | 2.973 | 2.975 | 2.9839 | 2.9889 | 2.9918 | 2.52 | 6.5
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 24 | 0.99381 | 9.7798 | 9.8249 | 9.8733 | 9.959 | 9.9956 | 2.82 | 5
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 19.2 | 0.99806 | 5.0002 | 5.0651 | 5.1376 | 5.2105 | 5.2657 | 3.56 | 5
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 8.4 | 0.99519 | 4.4631 | 4.4996 | 4.5191 | 4.5411 | 4.5699 | 3.84 | 1
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 8.4 | 0.99429 | 3.3115 | 3.3096 | 3.3186 | 3.3274 | 3.3278 | 3.2 | 2
Morven | Morven | 132/66 | 30 |  |  | 0 | 0.99964 | 7.7692 | 7.8267 | 7.8838 | 7.9128 | 7.9808 | 0 | 3
Albury | Corowa | 132/22 | 30 | 27/30 |  | 36 | 0.99949 | 13.0284 | 13.0883 | 13.0426 | 13.0383 | 13.0717 | 9.54 | 10
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 52.8 | 0.99255 | 34.6096 | 35.0155 | 35.5401 | 35.947 | 36.429 | 18.28 | 5.5
Albury | Mulwala | 132/22 | 30 | 30 |  | 36 | 0.99755 | 10.7997 | 10.8969 | 10.9925 | 11.1003 | 11.1919 | 7.66 | 4.5
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 84 | 0.9964 | 50.3496 | 51.6663 | 52.875 | 54.0382 | 55.3802 | 49.84 | 4
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 36 | 0.99846 | 11.3744 | 11.4666 | 11.5441 | 11.6333 | 11.6991 | 10.44 | 2.5
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 12 | 0.99952 | 3.937 | 3.9579 | 3.9713 | 4.0031 | 4.0307 | 2.34 | 23.5
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 12 | 0.99347 | 5.6991 | 5.901 | 6.0928 | 6.3273 | 6.5088 | 4.37 | 5
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 36 | 0.99967 | 17.7668 | 17.8363 | 17.7798 | 17.8796 | 17.9139 | 12.7 | 11
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 6 | 0.99778 | 2.8347 | 2.8442 | 2.8369 | 2.8366 | 2.8358 | 2.36 | 4.5
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 36 | 0.99183 | 9.5628 | 9.7422 | 9.8814 | 10.0744 | 10.2821 | 9.39 | 5.5
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 6 | 0.97629 | 2.7099 | 2.7138 | 2.7284 | 2.7457 | 2.7774 | 1.1 | 21
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0.89692 | 0.54596 | 0.54335 | 0.54192 | 0.54058 | 0.53837 | 0 | 6
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 30 | 0.95483 | 10.2875 | 10.4313 | 10.6633 | 10.7617 | 10.9748 | 0.41 | 2
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 9 | 0.97552 | 1.6558 | 1.6586 | 1.6613 | 1.6643 | 1.6459 | 0.87 | 1
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 15 | 0.86613 | 2.7977 | 2.8837 | 2.9501 | 3.0282 | 3.0916 | 1.31 | 5
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 3 | 0.98202 | 0.90346 | 0.91567 | 0.90731 | 0.92737 | 0.93797 | 0.11 | 5
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.79602 | 1.6579 | 1.6188 | 1.6022 | 1.5758 | 1.5462 | 0.51 | 4
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.8 | 0.94465 | 0.49756 | 0.49704 | 0.49857 | 0.49834 | 0.49978 | 0.24 | 4.5
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 36 | 0.98415 | 13.7313 | 13.7731 | 13.7891 | 13.8098 | 13.8219 | 1.1 | 18
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 12 | 0.98282 | 7.4016 | 7.4374 | 7.4805 | 7.5342 | 7.5804 | 3.53 | 8
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 19.2 | 0.99018 | 8.4361 | 8.4968 | 8.5553 | 8.6263 | 8.7054 | 3.82 | 6
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.2 | 0.97804 | 0.83873 | 0.85152 | 0.86616 | 0.88188 | 0.89868 | 0.36 | 6
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 15 | 0.98922 | 7.8648 | 8.0769 | 8.249 | 8.4676 | 8.6559 | 6.32 | 2
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 60 | 0.98839 | 20.6529 | 20.6733 | 20.7233 | 20.6587 | 20.7272 | 11.81 | 4
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 30 | 0.99997 | 12.4228 | 12.5425 | 12.5986 | 12.8278 | 12.9382 | 2.18 | 24
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | 0.98279 | 1.0974 | 1.1296 | 1.1798 | 1.2054 | 1.2489 | 0.61 | 3.5
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99931 | 10.2534 | 10.3216 | 10.3707 | 10.4514 | 10.5068 | 8.28 | 13
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 3 | 0.88251 | 0.85085 | 0.84732 | 0.84852 | 0.84759 | 0.84268 | 0.45 | 3
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0.93896 | 0.32073 | 0.32111 | 0.32084 | 0.32114 | 0.32214 | 0 | 3
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.97083 | 1.4639 | 1.5032 | 1.5564 | 1.5883 | 1.6573 | 0.36 | 1.5
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 11.4 | 0.99999 | 5.4043 | 5.5028 | 5.6023 | 5.7013 | 5.7605 | 2.18 | 2.5
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.96863 | 0.31128 | 0.31562 | 0.31873 | 0.3252 | 0.33204 | 0.15 | 1.5
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99171 | 16.4351 | 16.4128 | 16.4217 | 16.4031 | 16.3971 | 9.04 | 7.5
Yanco | Murrami | 33/11 | 5 | 5 |  | 6 | 0.7897 | 1.3952 | 1.4186 | 1.4482 | 1.4782 | 1.5003 | 0.55 | 6.5
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.97896 | 8.591 | 8.68 | 8.8284 | 8.9572 | 9.0932 | 5.72 | 5
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 7.5 | 0.94845 | 2.6174 | 2.6078 | 2.6001 | 2.5847 | 2.6099 | 0.97 | 3
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.985 | 2.1737 | 2.2234 | 2.281 | 2.3302 | 2.3882 | 1.87 | 5
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.99894 | 9.7906 | 9.9669 | 10.1497 | 10.2897 | 10.4695 | 1.13 | 3
Buronga | Powercor Robinvale 22kV Euston Distribution Supply | [5 empty] | 0.97746 | 3.0764 | 3.0977 | 3.0744 | 3.0837 | 3.0733 | 2.12 | 4
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply | [5 empty] | 0.97339 | 2.7526 | 2.7581 | 2.7632 | 2.7808 | 2.7845 | 1.33 | 12
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 36 | 0.99786 | 8.6627 | 8.8234 | 8.97 | 9.1128 | 9.2583 | 6.46 | 4
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 36 | 0.99681 | 4.3986 | 4.4485 | 4.5233 | 4.5737 | 4.6436 | 4.75 | 7.5
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.97666 | 1.4608 | 1.4543 | 1.4432 | 1.4459 | 1.4473 | 0.91 | 1
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0.92584 | 6.7728 | 6.7755 | 6.8108 | 6.8069 | 6.8354 | 0 | 39
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0.99756 | 0.33653 | 0.3277 | 0.33918 | 0.3365 | 0.34467 | 0 | 0.5

## Lines
Supply Area | Feeder # | Feeder Voltage kV | Feeder Origin | Feeder Destination | Summer | [5 empty] | Winter
[5 empty] | Line Rating | Line Forecast POE50 MVA |  |  |  |  | Line Rating | Line Forecast POE50 MVA
[5 empty] | MVA | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | MVA | 2025 | 2026 | 2027 | 2028 | 2029
Casino | 96L | 132 | Transgrid Casino 132kV 96L Tee | Casino ZS | 140 | 26.3452 | 26.4938 | 26.6642 | 26.7938 | 26.9877 | 157 | 23.8204 | 23.979 | 24.1941 | 24.3284 | 24.5629
Casino | 6501 | 66 | Casino ZS | Rappville Tee | 16 | 0.68618 | 0.69327 | 0.69608 | 0.69529 | 0.68926 | 25 | 0.63331 | 0.66844 | 0.69819 | 0.72275 | 0.75735
Casino | 8401 | 33 | Casino ZS | Mallanganee ZS | 4 | 2.7345 | 2.7432 | 2.755 | 2.7597 | 2.7769 | 6 | 2.65 | 2.6713 | 2.6979 | 2.7274 | 2.7408
Casino | 8402 | 33 | Mallanganee ZS | Bonalbo ZS | 4 | 1.7277 | 1.7307 | 1.7384 | 1.7387 | 1.7493 | 6 | 1.7085 | 1.7257 | 1.7435 | 1.7616 | 1.7756
Casino | 8403 | 33 | Bonalbo ZS | Urbenville ZS | 4 | 0.84471 | 0.84327 | 0.84621 | 0.84344 | 0.84823 | 7 | 0.97078 | 0.98922 | 1.0087 | 1.0285 | 1.0451
Coffs Harbour | 96C/2(D) | 132 | TransGrid 96C Armidale Coffs Harbour Dorrigo Tee | Dorrigo ZS | 41 | 2.405 | 2.3862 | 2.3875 | 2.3756 | 2.3668 | 76 | 2.6766 | 2.6745 | 2.6801 | 2.6781 | 2.6853
Coffs Harbour | 702 | 66 | Boambee South 132/66kV STS | Sawtell ZS | 61 | 9.296 | 9.3111 | 9.3451 | 9.306 | 9.3385 | 68 | 10.4235 | 10.5054 | 10.609 | 10.7446 | 10.8399
Coffs Harbour | 705 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 14.7937 | 14.8065 | 14.8905 | 14.8834 | 14.8893 | 58 | 15.8033 | 16.0215 | 16.2364 | 16.4778 | 16.6624
Coffs Harbour | 706 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 16.8484 | 16.863 | 16.9587 | 16.9505 | 16.9573 | 58 | 17.9983 | 18.2467 | 18.4915 | 18.7664 | 18.9766
Coffs Harbour | 7501 | 66 | Nana Glen ZS | Woolgoolga ZS | 29 | 5.5183 | 5.5231 | 5.5544 | 5.5517 | 5.5539 | 33 | 5.8949 | 5.9763 | 6.0565 | 6.1465 | 6.2153
Coffs Harbour | 7502 | 66 | Nana Glen ZS | Ulong Tee | 9 | 0.38683 | 0.38834 | 0.39065 | 0.3941 | 0.39595 | 15 | 0.49155 | 0.50124 | 0.51168 | 0.52317 | 0.53116
Coffs Harbour | 7502/1 | 66 | Ulong Tee | Ulong ZS | 9 | 0.38683 | 0.38834 | 0.39065 | 0.3941 | 0.39595 | 15 | 0.49155 | 0.50124 | 0.51168 | 0.52317 | 0.53116
Coffs Harbour | 7502/2 | 66 | Ulong Tee | Dorrigo ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | 7509 | 66 | Moonee ZS | Woolgoolga ZS | 30 | 10.1515 | 10.2843 | 10.4411 | 10.5922 | 10.7337 | 36 | 12.8136 | 13.109 | 13.3625 | 13.6542 | 13.9335
Coffs Harbour | 7510 | 66 | North Coffs ZS | Moonee ZS | 61 | 7.162 | 7.1682 | 7.2089 | 7.2055 | 7.2083 | 68 | 7.6508 | 7.7564 | 7.8605 | 7.9773 | 8.0667
Coffs Harbour | 703:NGN | 66 | TransGrid Coffs Harbour 132/66 kV STS | Nana Glen ZS | 62 | 9.0406 | 9.0484 | 9.0998 | 9.0954 | 9.099 | 69 | 9.6576 | 9.7909 | 9.9223 | 10.0698 | 10.1826
Coffs Harbour | 711:CHN | 66 | TransGrid Coffs Harbour 132/66 kV STS | North Coffs ZS | 62 | 18.1986 | 18.2143 | 18.3177 | 18.3089 | 18.3162 | 69 | 19.4406 | 19.709 | 19.9734 | 20.2703 | 20.4974
Coffs Harbour | 87C | 66 | North Coffs ZS | South Coffs ZS | 68 | 11.3888 | 11.3987 | 11.4634 | 11.4578 | 11.4624 | 68 | 12.1661 | 12.334 | 12.4995 | 12.6853 | 12.8274
Grafton | 825 | 66 | TransGrid Koolkhan 132/66kV STS | Koolkhan ZS | 62 | 19.0849 | 19.1351 | 19.1381 | 19.134 | 19.1424 | 69 | 15.8261 | 15.854 | 15.8911 | 15.8977 | 15.9616
Grafton | 826 | 66 | TransGrid Koolkhan 132/66kV STS | Grafton North ZS | 61 | 15.572 | 15.613 | 15.6154 | 15.612 | 15.6189 | 68 | 12.5972 | 12.6194 | 12.649 | 12.6542 | 12.7051
Grafton | 6503 | 66 | Grafton North ZS | South Grafton ZS | 24 | 10.1716 | 10.1984 | 10.2 | 10.1978 | 10.2022 | 25 | 7.3673 | 7.3803 | 7.3976 | 7.4006 | 7.4304
Grafton | 6504 | 66 | Five Mile Sw Stn | South Grafton ZS | 61 | 4.4042 | 4.4158 | 4.4165 | 4.4155 | 4.4175 | 68 | 3.1834 | 3.189 | 3.1965 | 3.1978 | 3.2107
Grafton | 6505 | 66 | Koolkhan SS | Grafton ZS | 52 | 16.9352 | 16.9798 | 16.9824 | 16.9788 | 16.9862 | 58 | 13.5977 | 13.6217 | 13.6536 | 13.6592 | 13.7142
Grafton | 6506 | 66 | Shannon Creek ZS | Nymboida ZS | 14 | 0.26215 | 0.26285 | 0.26289 | 0.26283 | 0.26294 | 21 | 0.36382 | 0.36446 | 0.36531 | 0.36546 | 0.36693
Grafton | 6508 | 66 | Maclean ZS | Yamba ZS | 28 | 11.1395 | 11.2375 | 11.3628 | 11.4049 | 11.5064 | 32 | 10.5345 | 10.5084 | 10.4682 | 10.4624 | 10.4671
Grafton | 6509 | 66 | Shannon Creek ZS | Five Mile Sw Stn | 14 | 1.2059 | 1.2091 | 1.2093 | 1.209 | 1.2095 | 21 | 1.046 | 1.0478 | 1.0503 | 1.0507 | 1.0549
Grafton | 6510 | 66 | Grafton North ZS | Five Mile Sw Stn | 28 | 5.5052 | 5.5197 | 5.5206 | 5.5194 | 5.5218 | 34 | 3.9565 | 3.9635 | 3.9728 | 3.9744 | 3.9904
Grafton | 896:MLN | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 21 | 9.0706 | 9.0944 | 9.0958 | 9.0939 | 9.0979 | 25 | 7.6402 | 7.6537 | 7.6716 | 7.6747 | 7.7056
Grafton | 8G1 | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 68 | 11.6397 | 11.6703 | 11.6721 | 11.6696 | 11.6747 | 68 | 9.6866 | 9.7038 | 9.7265 | 9.7305 | 9.7696
Grafton | 6402 | 33 | Maclean ZS | Yamba Tee | 8 | 0.47188 | 0.47312 | 0.47319 | 0.47309 | 0.4733 | 9 | 0.27286 | 0.27335 | 0.27399 | 0.2741 | 0.2752
Grafton | 6403 | 33 | Yamba Tee | Redcliff ZS | 3 | 0.47188 | 0.47312 | 0.47319 | 0.47309 | 0.4733 | 5 | 0.36382 | 0.36446 | 0.36531 | 0.36546 | 0.36693
Grafton | 6404 | 33 | Yamba Tee | Yamba ZS | 10 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7Y1 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 4.8197 | 4.8418 | 4.8609 | 4.8633 | 4.8557 | 12 | 4.0255 | 4.0449 | 4.0726 | 4.0896 | 4.0901
Hawks Nest | 7Y2 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 4.4204 | 4.4406 | 4.4582 | 4.4604 | 4.4534 | 12 | 3.692 | 3.7098 | 3.7352 | 3.7508 | 3.7512
Hawks Nest | 7V1 | 33 | Ausgrid Salt Ash ZS | Tee with 7Y1 | 7 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Herons Creek | 866:KEW | 66 | Herons Creek 132/66kV STS | Kew ZS | 16 | 12.1446 | 12.1499 | 12.2091 | 12.2258 | 12.2684 | 25 | 11.9345 | 12.1849 | 12.4913 | 12.7617 | 13.0292
Herons Creek | 871 | 66 | Kew ZS | Laurieton ZS | 36 | 7.7159 | 7.7299 | 7.7308 | 7.7377 | 7.7675 | 42 | 8.6353 | 8.6713 | 8.7598 | 8.8005 | 8.9021
Herons Creek | 862/1 | 66 | Kew ZS | Johns River ZS | 16 | 0.83858 | 0.83697 | 0.83434 | 0.83516 | 0.83602 | 25 | 1.0006 | 0.99793 | 0.99618 | 0.99047 | 0.98982
Herons Creek | 862/2 | 66 | TransGrid Taree 132/66/33kV STS | Johns River ZS | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Kempsey | 7R1 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 30 | 7.0903 | 7.2189 | 7.3336 | 7.4236 | 7.5248 | 34 | 7.6778 | 7.7801 | 7.9199 | 8.0366 | 8.1578
Kempsey | 7R2/1 | 33 | TransGrid Kempsey 132/33kV STS | North St Tee | 26 | 8.2066 | 8.3555 | 8.4882 | 8.5924 | 8.7096 | 29 | 8.4993 | 8.6125 | 8.7673 | 8.8965 | 9.0307
Kempsey | 7R2/2 | 33 | North St Tee | Smithtown ZS | 19 | 4.1033 | 4.1777 | 4.2441 | 4.2962 | 4.3548 | 21 | 4.9922 | 5.0587 | 5.1495 | 5.2254 | 5.3043
Kempsey | 7R2/3 | 33 | North St Tee | North St ZS | 10 | 4.043 | 4.1163 | 4.1817 | 4.233 | 4.2908 | 19 | 3.4756 | 3.5219 | 3.5851 | 3.638 | 3.6928
Kempsey | 7R3 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 26 | 7.1205 | 7.2496 | 7.3648 | 7.4551 | 7.5569 | 29 | 7.7094 | 7.8121 | 7.9525 | 8.0696 | 8.1914
Kempsey | 7R4 | 33 | TransGrid Kempsey 132/33kV STS | Munga ZS | 3 | 1.5168 | 1.514 | 1.5149 | 1.5217 | 1.5165 | 4 | 1.2702 | 1.3027 | 1.334 | 1.3748 | 1.4042
Kempsey | 7R5 | 33 | TransGrid Kempsey 132/33kV STS | North St ZS | 19 | 6.2153 | 6.3281 | 6.4286 | 6.5075 | 6.5963 | 21 | 6.4456 | 6.5314 | 6.6488 | 6.7468 | 6.8486
Kempsey | 7R6/1 | 33 | Prince St ZS | South West Rocks Tee | 15 | 5.1895 | 5.2836 | 5.3676 | 5.4334 | 5.5075 | 18 | 6.0348 | 6.1152 | 6.2251 | 6.3168 | 6.4121
Kempsey | 7R6/2 | 33 | South West Rocks Tee | South West Rocks ZS | 19 | 2.6249 | 2.6725 | 2.715 | 2.7483 | 2.7858 | 21 | 3.128 | 3.1697 | 3.2266 | 3.2742 | 3.3236
Kempsey | 7R6/3 | 33 | South West Rocks Tee | Smithtown ZS | 19 | 2.4439 | 2.4882 | 2.5277 | 2.5588 | 2.5937 | 21 | 2.7488 | 2.7855 | 2.8355 | 2.8773 | 2.9207
Kempsey | 7R7 | 33 | Prince St ZS | Crescent Head ZS | 5 | 1.5532 | 1.547 | 1.5458 | 1.5461 | 1.5443 | 8 | 1.9498 | 1.9608 | 1.9613 | 1.9613 | 1.966
Kempsey | 7R8 | 33 | Smithtown ZS | South West Rocks ZS | 30 | 3.1077 | 3.164 | 3.2143 | 3.2537 | 3.2981 | 34 | 3.6651 | 3.714 | 3.7807 | 3.8364 | 3.8943
Lismore | 9U8 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 183 | 52.6022 | 53.1147 | 53.6769 | 54.1931 | 54.8072 | 214 | 48.9652 | 49.2515 | 49.5389 | 49.923 | 50.1749
Lismore | 9U9 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 48.6788 | 49.1531 | 49.6734 | 50.1511 | 50.7194 | 143 | 45.2928 | 45.5577 | 45.8235 | 46.1788 | 46.4118
Lismore | 9W1 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 45.0461 | 45.485 | 45.9664 | 46.4085 | 46.9343 | 143 | 41.8925 | 42.1374 | 42.3833 | 42.7119 | 42.9274
Lismore | 9G2 | 132 | Ballina ZS | Lennox Head ZS | 124 | 11.6248 | 11.7381 | 11.8623 | 11.9764 | 12.1121 | 139 | 9.793 | 9.8503 | 9.9078 | 9.9846 | 10.035
Lismore | 9G3 | 132 | Lennox Head ZS | Suffolk Park ZS | 124 | 15.5482 | 15.6997 | 15.8658 | 16.0184 | 16.1999 | 139 | 14.2815 | 14.365 | 14.4488 | 14.5609 | 14.6344
Lismore | 9G4 | 132 | Suffolk Park ZS | Ewingsdale ZS | 124 | 21.6512 | 21.8621 | 22.0935 | 22.306 | 22.5588 | 139 | 20.5382 | 20.6583 | 20.7788 | 20.9399 | 21.0456
Lismore | 9G5 | 132 | Ewingsdale ZS | Mullumbimby ZS | 122 | 37.7806 | 38.1487 | 38.5525 | 38.9233 | 39.3643 | 137 | 39.0362 | 39.2644 | 39.4935 | 39.7997 | 40.0006
Lismore | 9U6 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 69.7488 | 70.4284 | 71.1738 | 71.8583 | 72.6725 | 123 | 65.287 | 65.6687 | 66.0519 | 66.564 | 66.8999
Lismore | 9U6/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 56.6709 | 57.2231 | 57.8287 | 58.3849 | 59.0464 | 123 | 53.0457 | 53.3558 | 53.6671 | 54.0833 | 54.3562
Lismore | 9U7 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 72.655 | 73.3629 | 74.1394 | 74.8524 | 75.7005 | 123 | 68.0072 | 68.4049 | 68.804 | 69.3375 | 69.6874
Lismore | 9U7/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 59.5771 | 60.1576 | 60.7943 | 61.379 | 62.0744 | 123 | 55.7659 | 56.092 | 56.4193 | 56.8568 | 57.1437
Lismore | 892 | 66 | Lismore 132/66kV STS | Woodburn ZS | 11 | 7.9343 | 7.9742 | 8.0118 | 8.0454 | 8.1227 | 19 | 7.0746 | 7.1163 | 7.1968 | 7.2569 | 7.3351
Lismore | 893 | 66 | Lismore 132/66kV STS | Casino ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Lismore | 894:LME | 66 | Lismore 132/66kV STS | Kyogle ZS | 11 | 8.6184 | 8.7573 | 8.9573 | 9.0132 | 9.1699 | 19 | 7.1174 | 7.1701 | 7.2401 | 7.3001 | 7.3458
Lismore | 0897:LME | 66 | Lismore 132/66kV STS | Alstonville ZS | 62 | 18.4544 | 18.6342 | 18.8314 | 19.0125 | 19.2279 | 69 | 18.362 | 18.4693 | 18.5771 | 18.7211 | 18.8156
Lismore | 8502 | 66 | Lismore East ZS | Alstonville ZS | 62 | 9.7358 | 9.8306 | 9.9347 | 10.0302 | 10.1439 | 69 | 10.2011 | 10.2607 | 10.3206 | 10.4006 | 10.4531
Lismore | 8503 | 66 | Ballina ZS | Alstonville ZS | 62 | 8.5733 | 8.6568 | 8.7484 | 8.8326 | 8.9327 | 69 | 8.1609 | 8.2086 | 8.2565 | 8.3205 | 8.3625
Lismore | 8507 | 66 | Alstonville ZS | Ballina ZS | 61 | 9.8811 | 9.9774 | 10.083 | 10.1799 | 10.2953 | 68 | 9.521 | 9.5767 | 9.6326 | 9.7073 | 9.7562
Lismore | 8510 | 66 | Lismore Sw Stn | East Lismore ZS | 61 | 22.2324 | 22.449 | 22.6866 | 22.9048 | 23.1644 | 68 | 21.8983 | 22.0264 | 22.1549 | 22.3267 | 22.4393
Lismore | 8511 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 19.4715 | 19.6613 | 19.8694 | 20.0604 | 20.2877 | 69 | 18.0899 | 18.1957 | 18.3019 | 18.4438 | 18.5368
Lismore | 8512 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 9.5002 | 9.5767 | 9.6742 | 9.742 | 9.8393 | 54 | 8.2187 | 8.3687 | 8.4745 | 8.6116 | 8.7715
Lismore | 8513 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 9.5002 | 9.5767 | 9.6742 | 9.742 | 9.8393 | 54 | 8.2187 | 8.3687 | 8.4745 | 8.6116 | 8.7715
Lismore | 8514 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 3.8889 | 3.9022 | 3.8835 | 3.8706 | 3.8981 | 68 | 4.3009 | 4.2781 | 4.259 | 4.2872 | 4.2864
Lismore | 8515 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 3.778 | 3.7916 | 3.773 | 3.7598 | 3.7875 | 68 | 4.2016 | 4.1801 | 4.162 | 4.1912 | 4.1912
Lismore | 8516 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 19.3262 | 19.5145 | 19.7211 | 19.9107 | 20.1363 | 69 | 17.9539 | 18.0589 | 18.1643 | 18.3051 | 18.3975
Nambucca Heads | 751 | 66 | TransGrid Nambucca 132/66 kV STS | Nambucca ZS | 15 | 7.3406 | 7.397 | 7.4759 | 7.5697 | 7.6354 | 25 | 8.6867 | 8.7366 | 8.8113 | 8.8677 | 8.9121
Port Macquarie | 70Y | 33 | Rocks Ferry ZS | Telegraph Point ZS | 8 | 1.8377 | 1.855 | 1.8669 | 1.8962 | 1.9197 | 12 | 1.779 | 1.833 | 1.8888 | 1.9428 | 1.9962
Port Macquarie | 701 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 22 | 10.1939 | 10.2064 | 10.2495 | 10.3353 | 10.3886 | 26 | 10.6703 | 10.7587 | 10.8952 | 11.0346 | 11.14
Port Macquarie | 703:BPM | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 8.4483 | 8.4587 | 8.4945 | 8.5656 | 8.6097 | 29 | 9.1344 | 9.2101 | 9.3269 | 9.4463 | 9.5365
Port Macquarie | 707 | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 9.5655 | 9.5772 | 9.6177 | 9.6982 | 9.7482 | 29 | 10.2661 | 10.3511 | 10.4825 | 10.6166 | 10.718
Port Macquarie | 708 | 33 | TransGrid Port Macquarie 132/33kV STS | Owen Street ZS | 26 | 11.1015 | 11.1151 | 11.1622 | 11.2556 | 11.3136 | 29 | 13.3378 | 13.4483 | 13.619 | 13.7932 | 13.925
Port Macquarie | 710 | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 31 | 12.079 | 12.0938 | 12.145 | 12.2466 | 12.3098 | 34 | 15.3587 | 15.486 | 15.6824 | 15.8831 | 16.0349
Port Macquarie | 711:CPM | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 20 | 12.0092 | 12.0239 | 12.0748 | 12.1759 | 12.2386 | 20 | 15.3587 | 15.486 | 15.6824 | 15.8831 | 16.0349
Port Macquarie | 712 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 12 | 6.7726 | 6.7809 | 6.8096 | 6.8666 | 6.902 | 14 | 7.0327 | 7.0909 | 7.1809 | 7.2728 | 7.3423
Port Macquarie | 715 | 33 | Clearwater ZS | Owen Street ZS | 31 | 5.0271 | 5.0333 | 5.0546 | 5.0969 | 5.1231 | 34 | 4.2034 | 4.2383 | 4.292 | 4.3469 | 4.3885
Port Macquarie | 719/1 | 33 | Clearwater ZS | Lake Cathie ZS | 20 | 5.2375 | 5.3286 | 5.4327 | 5.4991 | 5.5876 | 20 | 6.8333 | 7.1094 | 7.3691 | 7.6574 | 7.9236
Port Macquarie | 719/2 | 33 | Lake Cathie ZS | Laurieton ZS | 12 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0
Port Macquarie | 765 | 33 | Rocks Ferry ZS | Koree ZS | 9 | 4.5384 | 4.5439 | 4.5632 | 4.6013 | 4.6251 | 11 | 5.2543 | 5.2978 | 5.365 | 5.4337 | 5.4856
Port Macquarie | 784 | 33 | Koree ZS | Byabarra ZS | 9 | 1.187 | 1.1884 | 1.1934 | 1.2034 | 1.2096 | 11 | 1.2934 | 1.3041 | 1.3206 | 1.3375 | 1.3503
Stroud | 9C9/3 | 33 | Stroud 132/33kV STS | Dungog ZS | 27 | 7.8742 | 7.9335 | 7.9762 | 8.0416 | 8.0932 | 27 | 5.2751 | 5.323 | 5.3554 | 5.4009 | 5.4275
Stroud | 9C9/2 | 33 | Dungog ZS | Martins Creek ZS | 21 | 6.0724 | 6.091 | 6.0842 | 6.0986 | 6.1135 | 27 | 4.123 | 4.1831 | 4.2354 | 4.3062 | 4.3558
Stroud | STR4B3/1 | 33 | Stroud 132/33kV STS | Booral ZS | 7 | 5.2109 | 5.2431 | 5.2613 | 5.2985 | 5.3133 | 12 | 7.2685 | 7.3593 | 7.4445 | 7.5249 | 7.6202
Stroud | STR4B3/2 | 33 | Booral ZS | Bulahdelah ZS | 7 | 3.7382 | 3.7613 | 3.7744 | 3.8011 | 3.8117 | 12 | 5.2382 | 5.3037 | 5.365 | 5.423 | 5.4917
Stroud | STR4B4 | 33 | Stroud 132/33kV STS | Dungog ZS | 4 | 2.7257 | 2.7462 | 2.761 | 2.7836 | 2.8015 | 6 | 1.7584 | 1.7743 | 1.7851 | 1.8003 | 1.8092
Stroud | STR4B5/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 7.401 | 7.4467 | 7.4726 | 7.5254 | 7.5465 | 19 | 7.9994 | 8.0994 | 8.1931 | 8.2816 | 8.3865
Stroud | STR4B5/2 | 33 | Wards River Sw Stn | Stratford Tee | 19 | 8.3009 | 8.3917 | 8.5114 | 8.6055 | 8.685 | 21 | 7.5894 | 7.5948 | 7.5826 | 7.5892 | 7.6082
Stroud | STR4B5/2a | 33 | Stratford Tee | Stratford Coal ZS | 7 | 5.1957 | 5.2803 | 5.3783 | 5.4619 | 5.5489 | 12 | 4.9015 | 4.9067 | 4.8911 | 4.9001 | 4.9129
Stroud | STR4B5/3 | 33 | Stratford Tee | Gloucester ZS | 19 | 2.9371 | 2.9387 | 2.9527 | 2.9596 | 2.9492 | 21 | 2.5049 | 2.5094 | 2.5173 | 2.5206 | 2.5308
Stroud | STR4B6/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 8.5338 | 8.5865 | 8.6164 | 8.6772 | 8.7016 | 19 | 9.2582 | 9.3739 | 9.4823 | 9.5848 | 9.7062
Stroud | STR4B6/2 | 33 | Wards River Sw Stn | Gloucester ZS | 17 | 5.7015 | 5.7046 | 5.7316 | 5.7452 | 5.7249 | 19 | 4.8624 | 4.8713 | 4.8864 | 4.8929 | 4.9127
Stroud | STR4B7 | 33 | Stroud 132/33kV STS | Dungog ZS | 7 | 4.0885 | 4.1193 | 4.1415 | 4.1754 | 4.2022 | 12 | 3.1764 | 3.2052 | 3.2247 | 3.2521 | 3.2681
Stroud | STR4B8 | 33 | Stroud 132/33kV STS | Bulahdelah ZS | 7 | 4.72 | 4.7492 | 4.7657 | 4.7994 | 4.8128 | 12 | 6.2128 | 6.2904 | 6.3632 | 6.4319 | 6.5134
Stroud | 3801 | 33 | Bulahdelah ZS | Pacific Palms ZS | 7 | 4.0045 | 4.009 | 3.9874 | 4.0004 | 4.0004 | 12 | 4.7712 | 4.8142 | 4.8635 | 4.9563 | 4.9943
Stroud | 3803 | 33 | Bulahdelah ZS | Bungwahl Sw Stn | 7 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Stroud | BLH4B4 | 33 | Bulahdelah ZS | Hawks Nest 132/33kV STS | 7 | 0.26432 | 0.26595 | 0.26688 | 0.26876 | 0.26952 | 12 | 0.36546 | 0.37002 | 0.3743 | 0.37835 | 0.38314
Stroud | 7J1 | 33 | Ausgrid Recloser 33175 (Patterson) | Martins Creek Tee | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0
Stroud | 7J1/2 | 33 | Martins Creek Tee | Martins Creek ZS | 4 | 2.4336 | 2.432 | 2.4103 | 2.4071 | 2.4078 | 7 | 1.723 | 1.7493 | 1.7764 | 1.8041 | 1.8386
Stroud | 7J1/3 | 33 | Martins Creek Tee | Gresford ZS | 4 | 2.4336 | 2.432 | 2.4103 | 2.4071 | 2.4078 | 7 | 1.723 | 1.7493 | 1.7764 | 1.8041 | 1.8386
Taree | 861 | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 9.5454 | 9.622 | 9.6503 | 9.7118 | 9.8131 | 69 | 8.5737 | 8.6508 | 8.7483 | 8.8056 | 8.8989
Taree | 863:WTE | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 9.888 | 9.9674 | 9.9967 | 10.0604 | 10.1653 | 69 | 8.8039 | 8.8831 | 8.9831 | 9.042 | 9.1378
Taree | 867 | 66 | TransGrid Taree 132/66/33kV STS | Hallidays Point ZS | 34 | 13.4125 | 13.5202 | 13.5599 | 13.6463 | 13.7886 | 39 | 17.953 | 18.1145 | 18.3186 | 18.4386 | 18.6339
Taree | 867/1 | 66 | Hallidays Point Tee | Tuncurry ZS | 39 | 13.4125 | 13.5202 | 13.5599 | 13.6463 | 13.7886 | 43 | 11.8536 | 11.9602 | 12.0949 | 12.1742 | 12.3032
Taree | 868/1 | 66 | TransGrid Taree 132/66/33kV STS | Bohnock Tee | 36 | 15.7132 | 15.8393 | 15.8859 | 15.9871 | 16.1538 | 41 | 21.6932 | 21.8884 | 22.1349 | 22.28 | 22.516
Taree | 868/2 | 66 | Bohnock Tee | Bohnock ZS | 16 | 6.0254 | 6.1608 | 6.3158 | 6.4519 | 6.5849 | 26 | 7.0265 | 7.1788 | 7.3288 | 7.4635 | 7.6232
Taree | 868/3 | 66 | Bohnock Tee | Hallidays Point ZS | 38 | 11.5034 | 11.5958 | 11.6299 | 11.704 | 11.826 | 43 | 15.0184 | 15.1535 | 15.3242 | 15.4246 | 15.588
Taree | 872 | 66 | Tuncurry ZS | Forster ZS | 30 | 6.7552 | 6.8094 | 6.8295 | 6.873 | 6.9446 | 37 | 9.4944 | 9.5798 | 9.6877 | 9.7512 | 9.8545
Taree | 86C | 66 | Tuncurry ZS | Forster ZS | 42 | 5.923 | 5.9706 | 5.9882 | 6.0263 | 6.0891 | 46 | 8.4586 | 8.5347 | 8.6309 | 8.6874 | 8.7794
Taree | 86R | 66 | Hallidays Point ZS | Tuncurry ZS | 38 | 11.2587 | 11.349 | 11.3824 | 11.455 | 11.5744 | 43 | 15.7089 | 15.8502 | 16.0287 | 16.1338 | 16.3047
Taree | 7G2/1 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Tee | 22 | 6.5988 | 6.6045 | 6.6171 | 6.6274 | 6.6235 | 27 | 5.6955 | 5.753 | 5.8177 | 5.868 | 5.9202
Taree | 7G2/2 | 33 | Kanangra Tee | Coopernook ZS | 7 | 5.6429 | 5.6478 | 5.6586 | 5.6673 | 5.664 | 12 | 5.134 | 5.1858 | 5.2441 | 5.2895 | 5.3365
Taree | 7G2/3 | 33 | Coopernook ZS | Harrington ZS | 8 | 3.2121 | 3.2624 | 3.3062 | 3.366 | 3.418 | 13 | 3.6767 | 3.7834 | 3.906 | 4.0113 | 4.1124
Taree | 7G4 | 33 | Bootawa ZS | Wingham ZS | 18 | 2.621 | 2.6233 | 2.6283 | 2.6324 | 2.6308 | 21 | 2.46 | 2.4848 | 2.5128 | 2.5345 | 2.5571
Taree | 7G5 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Dr ZS | 17 | 9.7132 | 9.7216 | 9.7402 | 9.7552 | 9.7495 | 17 | 8.4497 | 8.5349 | 8.6309 | 8.7056 | 8.783
Taree | 7G1 | 33 | TransGrid Taree 132/66/33kV STS | Bootawa ZS | 17 | 7.0922 | 7.0983 | 7.1119 | 7.1229 | 7.1187 | 19 | 5.6688 | 5.7259 | 5.7904 | 5.8405 | 5.8924
Taree | 7G3 | 33 | TransGrid Taree 132/66/33kV STS | Wingham ZS | 18 | 7.4622 | 7.4687 | 7.4829 | 7.4945 | 7.4901 | 20 | 6.1501 | 6.2121 | 6.282 | 6.3363 | 6.3927
Terranora | 757 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 119 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 141.4214
Terranora | 758 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 119 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 142.8356
Terranora | 9501 | 66 | Terranora 110/66kV STS | Cudgen ZS | 59 | 24.3025 | 24.5272 | 24.6635 | 24.8127 | 24.9803 | 66 | 23.7083 | 23.8458 | 24.0599 | 24.2413 | 24.4628
Terranora | 9502 | 66 | Terranora 110/66kV STS | Murwillumbah ZS | 61 | 9.6956 | 9.7452 | 9.7777 | 9.8439 | 9.9067 | 68 | 11.0087 | 11.0545 | 11.1259 | 11.2019 | 11.2477
Terranora | 9503 | 66 | Terranora 110/66kV STS | Banora Pt ZS | 59 | 31.001 | 31.104 | 31.2192 | 31.3604 | 31.5061 | 66 | 24.3921 | 24.5824 | 24.7574 | 24.9298 | 25.1251
Terranora | 9504 | 66 | Terranora 110/66kV STS | Condong Sw Stn | 61 | 8.7261 | 8.7707 | 8.7999 | 8.8595 | 8.916 | 68 | 10.0079 | 10.0496 | 10.1145 | 10.1836 | 10.2252
Terranora | 9505 | 66 | Cudgen ZS | Banora Point ZS | 53 | 1.2208 | 1.2254 | 1.2299 | 1.2361 | 1.2424 | 59 | 1.0616 | 1.0686 | 1.076 | 1.0835 | 1.0907
Terranora | 9508 | 66 | Terranora 110/66kV STS | Tweed Heads ZS | 41 | 17.2021 | 17.3053 | 17.4164 | 17.5078 | 17.625 | 46 | 12.2977 | 12.3378 | 12.3828 | 12.4081 | 12.4406
Terranora | 9510 | 66 | Banora Point ZS | Tweed Heads South ZS | 43 | 14.9716 | 15.0231 | 15.095 | 15.1937 | 15.3231 | 50 | 13.1901 | 13.2498 | 13.3004 | 13.3954 | 13.4741
Terranora | 9514 | 66 | Condong Sw Stn | Murwillumbah ZS | 61 | 16.4826 | 16.5669 | 16.6221 | 16.7346 | 16.8413 | 68 | 18.0142 | 18.0892 | 18.206 | 18.3305 | 18.4054
Terranora | 9516 | 66 | Tweed Head South ZS | Tweed Heads ZS | 43 | 4.0957 | 4.1203 | 4.1468 | 4.1685 | 4.1964 | 50 | 2.928 | 2.9376 | 2.9483 | 2.9543 | 2.962
Terranora | 9406 | 33 | Cudgen ZS | Casuarina Sw Stn | 17 | 11.0555 | 11.073 | 11.1621 | 11.1623 | 11.2096 | 19 | 12.0031 | 12.2108 | 12.4407 | 12.6739 | 12.9038
Terranora | 9407 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Terranora | 9409 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 11.0555 | 11.073 | 11.1621 | 11.1623 | 11.2096 | 20 | 12.0031 | 12.2108 | 12.4407 | 12.6739 | 12.9038
Armidale | 661/1 | 66 | TransGrid Armidale 330/132/66kV STS | Hillgrove Tee | 20 | 0.83009 | 0.83533 | 0.84026 | 0.8468 | 0.85096 | 24 | 0.94437 | 0.94773 | 0.94787 | 0.95374 | 0.95782
Armidale | 661/2 | 66 | Hillgrove Tee | Hillgrove ZS | 16 | 0.35575 | 0.358 | 0.36011 | 0.36291 | 0.3647 | 20 | 0.38633 | 0.38771 | 0.38777 | 0.39016 | 0.39184
Armidale | 661/3 | 66 | Hillgrove Tee | Oaky ZS | 20 | 0.50398 | 0.50717 | 0.51016 | 0.51413 | 0.51665 | 24 | 0.55804 | 0.56002 | 0.56011 | 0.56357 | 0.56598
Armidale | 662/1 | 66 | TransGrid Armidale 330/132/66kV STS | Uralla Tee | 12 | 5.8775 | 5.8911 | 5.9028 | 5.9267 | 5.9431 | 17 | 7.6365 | 7.7035 | 7.7782 | 7.8518 | 7.9116
Armidale | 662/2 | 66 | Uralla Tee | Uralla ZS | 9 | 3.0146 | 3.0139 | 3.0119 | 3.0317 | 3.0283 | 15 | 3.8419 | 3.8562 | 3.885 | 3.9015 | 3.9213
Armidale | 662/4 | 66 | Uralla Tee | Walcha South ZS | 9 | 2.8763 | 2.8906 | 2.9036 | 2.9082 | 2.9274 | 15 | 3.8122 | 3.8623 | 3.9059 | 3.9613 | 3.9989
Armidale | 664 | 66 | TransGrid Armidale 330/132/66kV STS | Galloway St ZS | 28 | 13.6965 | 13.783 | 13.8643 | 13.9722 | 14.0408 | 34 | 21.5059 | 21.5823 | 21.5857 | 21.7192 | 21.8122
Armidale | 665 | 66 | TransGrid Armidale 330/132/66kV STS | Madgwick Dr ZS | 21 | 8.8049 | 8.8605 | 8.9128 | 8.9821 | 9.0263 | 39 | 12.0622 | 12.1051 | 12.1069 | 12.1818 | 12.234
Armidale | 66C | 66 | Miller St ZS | Madgwick Dr ZS | 21 | 1.7491 | 1.7602 | 1.7706 | 1.7843 | 1.7931 | 39 | 3.3053 | 3.317 | 3.3176 | 3.3381 | 3.3524
Armidale | 66F | 66 | Galloway St ZS | Miller St ZS | 15 | 6.285 | 6.3247 | 6.362 | 6.4115 | 6.443 | 25 | 8.4564 | 8.4865 | 8.4878 | 8.5403 | 8.5768
Bathurst | 81H | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 62 | 7.7429 | 7.7795 | 7.906 | 7.8305 | 7.8913 | 69 | 8.6744 | 8.8085 | 8.9096 | 9.0219 | 9.1425
Bathurst | 81G | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 64 | 11.0613 | 11.1136 | 11.2943 | 11.1865 | 11.2733 | 71 | 12.392 | 12.5835 | 12.728 | 12.8885 | 13.0608
Bathurst | 81F | 66 | TransGrid Panorama 132/66kV STS | Russell St ZS | 64 | 25.8068 | 25.7707 | 25.822 | 25.8568 | 25.8837 | 71 | 31.4229 | 31.5238 | 31.5636 | 31.6958 | 31.7718
Bathurst | 81J | 66 | Raglan ZS | Russell St ZS | 64 | 4.9337 | 4.9267 | 4.9366 | 4.9432 | 4.9484 | 71 | 6.0073 | 6.0266 | 6.0342 | 6.0595 | 6.074
Bathurst | 81L | 66 | TransGrid Panorama 132/66kV STS | Raglan ZS | 64 | 15.9395 | 15.9172 | 15.9489 | 15.9704 | 15.987 | 71 | 19.4083 | 19.4706 | 19.4951 | 19.5768 | 19.6237
Bathurst | 81C | 66 | TransGrid Panorama 132/66kV STS | Blayney ZS | 25 | 12.8571 | 12.9538 | 12.9911 | 13.0485 | 13.1769 | 29 | 15.9756 | 16.1478 | 16.2276 | 16.3358 | 16.4122
Bathurst | 66:MAN | 66 | Blayney ZS | Mandurama ZS | 9 | 2.1592 | 2.1627 | 2.1664 | 2.1706 | 2.1733 | 15 | 2.5042 | 2.518 | 2.5298 | 2.5408 | 2.5556
Beryl | 94M/4 | 132 | TransGrid 94M Mudgee Tee | Mudgee ZS | 128 | 23.516 | 23.7239 | 23.7458 | 23.7441 | 23.6697 | 143 | 24.6375 | 25.0023 | 25.4433 | 25.8657 | 26.2356
Beryl | 851/1 | 66 | TransGrid Beryl 132/66kV STS | Gulgong ZS | 28 | 2.9209 | 2.9213 | 2.9275 | 2.9506 | 2.9622 | 32 | 3.4718 | 3.4538 | 3.476 | 3.4723 | 3.4896
Beryl | 851/2 | 66 | Gulgong ZS | Mudgee ZS | 28 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0
Beryl | 852 | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Beryl | 86J | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 61 | 13.1391 | 13.1256 | 13.1085 | 13.1074 | 13.1097 | 68 | 14.0161 | 14.1556 | 14.2995 | 14.4426 | 14.6074
Beryl | 85A | 66 | Dunedoo ZS | Coonabarabran ZS | 11 | 8.9846 | 8.9701 | 8.9609 | 8.9516 | 8.9596 | 19 | 9.5488 | 9.6215 | 9.7108 | 9.7881 | 9.8767
Beryl | 80L | 66 | Ulan Sw Stn | Ulan Town ZS | 15 | 2.4072 | 2.4115 | 2.4163 | 2.4214 | 2.4214 | 25 | 3.088 | 3.1868 | 3.2775 | 3.3377 | 3.4298
Beryl | 80R | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 64 | 44.3431 | 44.3891 | 44.4734 | 44.4546 | 44.5444 | 71 | 43.0469 | 43.0583 | 43.1014 | 43.262 | 43.2201
Beryl | 80U | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 61 | 32.8727 | 33.3264 | 33.7837 | 34.1812 | 34.6536 | 68 | 36.1136 | 37.0081 | 37.9709 | 38.8508 | 39.8497
Beryl | 80T | 66 | Ulan Sw Stn | Moolarben No1 Mine ZS | 43 | 31.6327 | 31.7827 | 31.9429 | 32.1042 | 32.2204 | 54 | 32.9394 | 33.498 | 34.0482 | 34.573 | 35.0882
Beryl | 80W | 66 | Moolarben No1 Mine ZS | Moolarben No2 Mine ZS | 43 | 13.8463 | 13.8302 | 13.8799 | 13.8856 | 13.8764 | 54 | 14.6361 | 14.6744 | 14.8015 | 14.9638 | 15.0179
Beryl | 80X | 66 | Moolarben No2 Mine ZS | Wilpinjong Mine ZS | 43 | 5.2877 | 5.2908 | 5.2922 | 5.2939 | 5.3021 | 54 | 5.4377 | 5.4341 | 5.4493 | 5.4425 | 5.4608
Broken Hill | X4 | 220 | TransGrid Broken Hill 220/22kV STS | Perilya Mine | 213 | 24.6404 | 24.6184 | 24.6199 | 24.604 | 24.618 | 238 | 24.2459 | 24.278 | 24.261 | 24.2787 | 24.2447
Broken Hill | 5B1:PPL | 66 | Pinnacles Place ZS | Mt Gipps ZS | 19 | 6.383 | 7.531 | 7.589 | 7.6932 | 7.7829 | 33 | 5.6948 | 6.3532 | 6.4169 | 6.4745 | 6.5347
Broken Hill | 5B1:MTG | 66 | Mt Gipps ZS | Sunset Strip ZS | 19 | 4.4739 | 5.5777 | 5.6071 | 5.6826 | 5.7353 | 33 | 4.1636 | 4.7573 | 4.7875 | 4.7934 | 4.8034
Broken Hill | 5B1:SUN | 66 | Sunset Strip ZS | Menindee ZS | 6 | 0.88265 | 0.88778 | 0.89355 | 0.90264 | 0.91015 | 9 | 0.71256 | 0.71336 | 0.71692 | 0.71775 | 0.71906
Dubbo | 94J/3 | 132 | 94J Tee | Dubbo South ZS | 106 | 43.0319 | 43.2662 | 43.6482 | 49.5644 | 55.5495 | 119 | 37.4733 | 37.5883 | 42.8693 | 48.3072 | 48.4494
Dubbo | 943/2 | 132 | Dubbo South ZS | Narromine South Sw Stn | 106 | 30.593 | 30.7596 | 31.0311 | 35.2372 | 39.4922 | 119 | 25.3591 | 25.4369 | 29.0107 | 32.6906 | 32.7869
Dubbo | 94W/1 | 132 | Dubbo 132/66kV STS | Nevertire Tee | 128 | 138.7605 | 138.8157 | 138.7927 | 138.8307 | 138.8515 | 143 | 119.2092 | 119.2309 | 119.2202 | 119.2605 | 119.318
Dubbo | 94W/2 | 132 | Nevertire Tee | Nevertire ZS | 124 | 6.7229 | 6.7108 | 6.7553 | 6.7654 | 6.7728 | 139 | 8.3338 | 8.3794 | 8.3693 | 8.3554 | 8.3557
Dubbo | 94W/3 | 132 | Nevertire Tee | Nevertire Sw Stn | 128 | 144.9569 | 144.9569 | 144.9569 | 144.9569 | 144.9569 | 143 | 125.4407 | 125.4407 | 125.4407 | 125.4407 | 125.4407
Dubbo | 9GX | 132 | Nevertire Sw Stn | Nyngan 132/66kV STS | 128 | 55.2922 | 55.5782 | 55.8272 | 56.0929 | 56.3769 | 143 | 47.9941 | 48.2833 | 48.5336 | 48.6758 | 48.8926
Dubbo | 9GP | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 12.2521 | 12.2122 | 12.2801 | 12.2761 | 12.1871 | 139 | 12.6799 | 12.7908 | 12.9403 | 13.1022 | 13.1275
Dubbo | 9GR | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GT | 132 | Dubbo West ZS | Narromine South Sw Stn | 140 | 42.7992 | 42.7896 | 42.8647 | 42.89 | 42.8585 | 157 | 41.9665 | 42.189 | 42.5139 | 42.6951 | 42.8534
Dubbo | 9GU | 132 | Narromine South Sw Stn | Nyngan 132/66kV STS | 106 | 67.2813 | 67.3325 | 67.3358 | 67.3908 | 67.5095 | 119 | 64.4346 | 64.6826 | 65.0696 | 65.1137 | 65.4086
Dubbo | 9GW | 132 | Dubbo 132/66kV STS | Dubbo West ZS | 140 | 33.2825 | 33.4637 | 33.7592 | 38.335 | 42.964 | 157 | 32.9506 | 33.0518 | 37.6954 | 42.477 | 42.6021
Dubbo | 812 | 66 | Yarrandale ZS | Gilgandra ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Dubbo | 815 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 10.1956 | 10.1259 | 10.0442 | 9.985 | 9.9835 | 54 | 8.941 | 8.9209 | 8.9136 | 8.8586 | 8.8497
Dubbo | 816 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 10.1956 | 10.1259 | 10.0442 | 9.985 | 9.9835 | 54 | 8.941 | 8.9209 | 8.9136 | 8.8586 | 8.8497
Dubbo | 813:EUL | 66 | Eulomogo ZS | Geurie Tee | 12 | 1.4974 | 1.5145 | 1.5129 | 1.5155 | 1.5221 | 18 | 1.2281 | 1.2257 | 1.2306 | 1.2333 | 1.2351
Dubbo | 813/1:GUE | 66 | Geurie Tee | Geurie ZS | 16 | 1.4974 | 1.5145 | 1.5129 | 1.5155 | 1.5221 | 27 | 1.2281 | 1.2257 | 1.2306 | 1.2333 | 1.2351
Dubbo | 814/1 | 66 | Gilgandra ZS | Gulargambone ZS | 11 | 7.6253 | 7.6687 | 7.7072 | 7.7411 | 7.7822 | 19 | 6.8421 | 6.8615 | 6.8788 | 6.9062 | 6.9267
Dubbo | 814/2 | 66 | Gulargambone ZS | Coonamble ZS | 11 | 5.9793 | 6.0312 | 6.0764 | 6.1197 | 6.1677 | 19 | 5.3856 | 5.4172 | 5.4482 | 5.4864 | 5.5212
Dubbo | 81M | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 9.4557 | 9.4531 | 9.5042 | 9.5109 | 9.5516 | 39 | 8.7336 | 8.7492 | 8.7595 | 8.7647 | 8.7791
Dubbo | 81P | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 61 | 9.9821 | 10.0064 | 10.0262 | 10.0572 | 10.0697 | 68 | 9.0243 | 9.0399 | 9.0708 | 9.1016 | 9.1233
Dubbo | 81R | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 9.4557 | 9.4531 | 9.5042 | 9.5109 | 9.5516 | 39 | 8.7336 | 8.7492 | 8.7595 | 8.7647 | 8.7791
Dubbo | 81X | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 28 | 12.2003 | 12.2301 | 12.2543 | 12.2922 | 12.3074 | 34 | 11.0297 | 11.0487 | 11.0866 | 11.1242 | 11.1507
Dubbo | 81T | 66 | Yarrandale ZS | Gilgandra ZS | 43 | 14.6475 | 14.7181 | 14.7712 | 14.8637 | 14.9107 | 54 | 13.2788 | 13.3402 | 13.4055 | 13.4822 | 13.5421
Forbes | 858 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 13.9883 | 14.034 | 14.0757 | 14.1163 | 14.1487 | 34 | 11.5559 | 11.5832 | 11.5885 | 11.5992 | 11.6306
Forbes | 859 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Forbes | 893/5 | 66 | TransGrid Forbes 132/66kV STS | Payten's Bridge ZS | 12 | 5.8119 | 5.8549 | 5.8205 | 5.8174 | 5.8008 | 18 | 4.2093 | 4.2043 | 4.2151 | 4.2273 | 4.2532
Forbes | 894:CDN | 66 | Condobolin ZS | Lake Cargelligo ZS | 15 | 3.6824 | 3.693 | 3.7131 | 3.7349 | 3.7291 | 25 | 3.4096 | 3.4211 | 3.4221 | 3.4292 | 3.4269
Forbes | 896:WJL | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 20 | 25.4558 | 25.4558 | 25.4558 | 25.4558 | 25.4558 | 24 | 28.2843 | 28.2843 | 28.2843 | 28.2843 | 28.2843
Forbes | 897:CDN | 66 | West Jemalong ZS | Condobolin ZS | 20 | 10.9215 | 10.9295 | 10.9465 | 10.9424 | 10.9511 | 24 | 10.6573 | 10.6827 | 10.6931 | 10.7176 | 10.7399
Forbes | 89H | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 43 | 42.4264 | 42.4264 | 42.4264 | 42.4264 | 42.4264 | 54 | 43.8406 | 43.8406 | 43.8406 | 43.8406 | 43.8406
Glen Innes | 886 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 70 | 5.1157 | 5.1303 | 5.153 | 5.1671 | 5.1876 | 78 | 6.7621 | 6.8732 | 6.9726 | 7.0935 | 7.1855
Glen Innes | 887 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 19 | 6.0896 | 6.1069 | 6.134 | 6.1508 | 6.1752 | 33 | 8.0494 | 8.1817 | 8.3 | 8.4439 | 8.5534
Glen Innes | 6NY | 66 | Glen Innes ZS | Guyra ZS | 11 | 3.8426 | 3.8994 | 4.0114 | 4.0916 | 4.157 | 19 | 4.5852 | 4.641 | 4.6892 | 4.7476 | 4.8022
Glen Innes | 6NE | 66 | Glen Innes ZS | Emmaville ZS | 17 | 1.0299 | 1.0328 | 1.0374 | 1.0402 | 1.0443 | 30 | 1.2577 | 1.2784 | 1.2969 | 1.3194 | 1.3365
Glen Innes | 6AE/A | 66 | Pindari ZS | Ashford ZS | 17 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0
Glen Innes | 6AE/E | 66 | Emmaville ZS | Pindari ZS | 17 | 0.35821 | 0.35923 | 0.36082 | 0.36181 | 0.36325 | 30 | 0.39951 | 0.40608 | 0.41195 | 0.41909 | 0.42452
Gunnedah | 877 | 66 | TransGrid Gunnedah 132/66kV STS | Keepit Dam ZS | 10 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 16 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 0.28284
Gunnedah | 88G/1 | 66 | Gunnedah ZS | Emerald Hill Sw Stn | 24 | 19.5037 | 19.4253 | 19.3363 | 19.27 | 19.1699 | 29 | 20.9839 | 21.0065 | 21.0265 | 21.0676 | 21.1004
Gunnedah | 88G/2 | 66 | Emerald Hill Sw Stn | Boggabri ZS | 24 | 3.2597 | 3.2556 | 3.2511 | 3.2777 | 3.2607 | 29 | 4.9419 | 5.0096 | 5.0731 | 5.1676 | 5.2531
Gunnedah | 88K | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 21.5239 | 21.5207 | 21.5542 | 21.545 | 21.5482 | 68 | 21.8348 | 21.9991 | 22.1806 | 22.4248 | 22.635
Gunnedah | 88L | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 21.5239 | 21.5207 | 21.5542 | 21.545 | 21.5482 | 68 | 21.8348 | 21.9991 | 22.1806 | 22.4248 | 22.635
Inverell | 734 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 17.2705 | 17.5376 | 17.8623 | 18.1472 | 18.54 | 71 | 19.5867 | 20.111 | 20.4603 | 20.7122 | 20.9391
Inverell | 735 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 17.5491 | 17.8204 | 18.1504 | 18.4399 | 18.839 | 71 | 19.9027 | 20.4354 | 20.7903 | 21.0463 | 21.2769
Inverell | 6AB | 66 | Borthwick St ZS | Ashford ZS | 17 | 6.3024 | 6.3998 | 6.5183 | 6.6223 | 6.7656 | 30 | 5.7655 | 5.9198 | 6.0226 | 6.0967 | 6.1635
Inverell | 6AF/A | 66 | Ashford ZS | Wallangra ZS | 11 | 0.87049 | 0.88395 | 0.90032 | 0.91468 | 0.93447 | 19 | 1.0267 | 1.0542 | 1.0725 | 1.0857 | 1.0976
Inverell | 6AF/F | 66 | Wallangra ZS | Coolatai Sw Stn | 11 | 0.73121 | 0.74252 | 0.75627 | 0.76833 | 0.78496 | 19 | 0.86877 | 0.89202 | 0.90751 | 0.91869 | 0.92875
Inverell | 6AX | 66 | Ashford ZS | Texas ZS | 9 | 5.2578 | 5.3391 | 5.4379 | 5.5246 | 5.6442 | 15 | 3.9095 | 4.0141 | 4.0838 | 4.1341 | 4.1794
Inverell | 6BC | 66 | Borthwick St ZS | Copeton ZS | 21 | 0.80085 | 0.81323 | 0.82829 | 0.8415 | 0.85972 | 41 | 0.98724 | 1.0137 | 1.0313 | 1.044 | 1.0554
Inverell | 6BD | 66 | Borthwick St ZS | Bundarra ZS | 14 | 0.90531 | 0.91931 | 0.93633 | 0.95126 | 0.97185 | 21 | 1.2242 | 1.2569 | 1.2788 | 1.2945 | 1.3087
Inverell | 6BW | 66 | Borthwick St ZS | Warialda ZS | 15 | 6.9291 | 7.0362 | 7.1665 | 7.2808 | 7.4384 | 25 | 6.8317 | 7.0145 | 7.1364 | 7.2242 | 7.3034
Inverell | 6FH | 66 | Coolatai Sw Stn | Yallaroi ZS | 20 | 2.1936 | 2.2276 | 2.2688 | 2.305 | 2.3549 | 39 | 2.2509 | 2.3111 | 2.3513 | 2.3802 | 2.4063
Inverell | 6FW | 66 | Warialda ZS | Coolatai Sw Stn | 11 | 1.6713 | 1.6972 | 1.7286 | 1.7562 | 1.7942 | 19 | 1.3426 | 1.3786 | 1.4025 | 1.4198 | 1.4353
Inverell | 6HG | 66 | Yallaroi ZS | Goondiwindi ZS | 20 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Inverell | 6WK | 66 | Warialda ZS | Bingara ZS | 11 | 2.6811 | 2.7226 | 2.773 | 2.8172 | 2.8782 | 19 | 2.8827 | 2.9599 | 3.0113 | 3.0484 | 3.0818
Molong | 8C1 | 66 | TransGrid Molong 132/66kV STS | Cumnock / Orange West Tee | 61 | 2.3524 | 2.3954 | 2.4438 | 2.4493 | 2.4994 | 68 | 1.8678 | 1.9214 | 1.9799 | 2.0226 | 2.0667
Molong | 8C1/3 | 66 | Cumnock / Orange West Tee | Cumnock ZS | 9 | 2.3524 | 2.3954 | 2.4438 | 2.4493 | 2.4994 | 15 | 1.8678 | 1.9214 | 1.9799 | 2.0226 | 2.0667
Molong | 8C1/4 | 66 | Cumnock / Orange West Tee | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Moree | 876 | 66 | TransGrid Moree 132/66kV STS | Moree Solar Farm | 70 | 57.3183 | 57.3327 | 57.2826 | 57.337 | 57.4828 | 78 | 57.8524 | 57.7453 | 57.6659 | 57.7539 | 57.7447
Moree | 87J | 66 | Moree Solar Farm | Bellata ZS | 25 | 1.1423 | 1.1475 | 1.1461 | 1.15 | 1.1547 | 27 | 0.92806 | 0.94553 | 0.95689 | 0.97218 | 0.98711
Moree | 721 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 10.4036 | 11.5931 | 14.1286 | 16.4765 | 18.5389 | 71 | 9.442 | 10.5009 | 13.0792 | 15.3553 | 17.4348
Moree | 722 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 10.9726 | 12.1698 | 14.7103 | 17.0666 | 19.1354 | 71 | 9.9583 | 11.0179 | 13.6033 | 15.8837 | 17.9703
Moree | 881/1 | 66 | TransGrid Moree 132/66kV STS | Ashley Tee | 15 | 5.5037 | 5.5252 | 5.4885 | 5.594 | 5.5614 | 25 | 9.7567 | 9.7536 | 9.734 | 9.7951 | 9.6819
Moree | 881/2 | 66 | Ashley Tee | Ashley ZS | 10 | 2.6361 | 2.645 | 2.6029 | 2.6941 | 2.657 | 16 | 3.8626 | 3.8508 | 3.8336 | 3.8981 | 3.7793
Moree | 6PU | 66 | Ashley Tee | Mungindi ZS | 10 | 2.6387 | 2.6484 | 2.6516 | 2.6661 | 2.6682 | 16 | 5.702 | 5.7102 | 5.7064 | 5.7058 | 5.7076
Moree | 723:WTR/1 | 66 | TransGrid Moree 132/66kV STS | Wathagar ZS | 12 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 19 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Moree | 723:WTR/2 | 66 | Wathagar ZS | Wenna ZS | 15 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 25 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Narrabri | 879 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 18 | 3.8924 | 3.8956 | 3.9037 | 3.8948 | 3.8968 | 22 | 5.184 | 5.2591 | 5.29 | 5.3425 | 5.3964
Narrabri | 882 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 64 | 7.5685 | 7.5748 | 7.5905 | 7.5732 | 7.5771 | 71 | 10.08 | 10.2261 | 10.2861 | 10.3881 | 10.4929
Narrabri | 885 | 66 | Burren Junction ZS | Merrywinebone ZS | 15 | 1.5275 | 1.5469 | 1.5677 | 1.5886 | 1.6014 | 25 | 2.5602 | 2.5609 | 2.5574 | 2.562 | 2.5537
Narrabri | 833:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 7.6498 | 7.6268 | 7.6209 | 7.6227 | 7.6494 | 43 | 8.6885 | 8.6933 | 8.7103 | 8.6727 | 8.6823
Narrabri | 834:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 7.6498 | 7.6268 | 7.6209 | 7.6227 | 7.6494 | 43 | 8.6885 | 8.6933 | 8.7103 | 8.6727 | 8.6823
Narrabri | 861/1 | 66 | TransGrid Narrabri 132/66kV STS | Wilga Park ZS | 64 | 34.9303 | 35.0706 | 34.9165 | 35.0132 | 34.9541 | 71 | 37.5689 | 38.2998 | 38.8959 | 39.3783 | 39.8737
Narrabri | 861/2 | 66 | Wilga Park ZS | Walgett ZS | 64 | 11.7635 | 11.8684 | 11.9543 | 12.0333 | 12.1622 | 71 | 11.3553 | 11.5114 | 11.7151 | 11.8758 | 12.0778
Narrabri | 88F | 66 | Narrabri Sw Stn | Boggabri ZS | 24 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0
Narrabri | 878/3 | 66 | TransGrid Narrabri 132/66kV STS | Narrabri Sw Stn | 61 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 68 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 26.4458
Narrabri | 88C | 66 | Narrabri Sw Stn | Narrabri Coal | 53 | 26.163 | 26.163 | 26.163 | 26.163 | 26.163 | 61 | 26.163 | 26.163 | 26.163 | 26.163 | 26.163
Narrabri | 880/1 | 66 | Wee Waa ZS | Burren Junction ZS | 13 | 3.1137 | 3.1217 | 3.1211 | 3.1262 | 3.1251 | 18 | 3.771 | 3.7717 | 3.7707 | 3.7788 | 3.7672
Narrabri | 880/2 | 66 | Burren Junction ZS | Walgett ZS | 13 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Narrabri | 890:BRE | 66 | Walgett ZS | Brewarrina ZS | 15 | 2.852 | 2.8914 | 2.9177 | 2.9648 | 2.9866 | 25 | 2.4342 | 2.4505 | 2.477 | 2.4963 | 2.5205
Narrabri | 895:LGR | 66 | Walgett ZS | Lightning Ridge ZS | 15 | 3.1595 | 3.1755 | 3.1909 | 3.2107 | 3.2295 | 25 | 3.1544 | 3.1792 | 3.2098 | 3.2264 | 3.2544
Nyngan | 9UT | 132 | Nyngan 132/66kV STS | Nyngan Solar Farm | 106 | 35.4564 | 35.7596 | 36.0429 | 36.3261 | 36.6048 | 119 | 28.5367 | 28.7276 | 28.8155 | 28.9395 | 29.0416
Nyngan | 9UW | 132 | Nyngan Solar Farm | Scrubby Valley Sw Stn | 106 | 35.4564 | 35.7596 | 36.0429 | 36.3261 | 36.6048 | 119 | 28.5367 | 28.7276 | 28.8155 | 28.9395 | 29.0416
Nyngan | 946/2 | 132 | Scrubby Valley Sw Stn | Cobar CSA ZS | 106 | 21.9494 | 22.3224 | 22.5548 | 22.9484 | 23.2588 | 119 | 18.2474 | 18.3337 | 18.3866 | 18.4021 | 18.4036
Nyngan | 946/3 | 132 | Scrubby Valley Sw Stn | Cobar Peak ZS | 102 | 15.6825 | 15.738 | 15.9119 | 15.9686 | 16.073 | 114 | 11.2606 | 11.3854 | 11.4355 | 11.5629 | 11.6868
Nyngan | 94R | 132 | Cobar CSA ZS | Cobar Elura ZS | 128 | 2.1089 | 2.1531 | 2.1735 | 2.2009 | 2.1928 | 143 | 1.9189 | 1.9351 | 1.9176 | 1.8513 | 1.7948
Nyngan | 811 | 66 | Nyngan 132/66kV STS | Cobar Town ZS | 10 | 7.4896 | 7.416 | 7.3595 | 7.3252 | 7.2723 | 16 | 7.1432 | 7.1477 | 7.1461 | 7.1515 | 7.1593
Nyngan | 854 | 66 | Nyngan 132/66kV STS | Nyngan Town ZS | 15 | 7.5002 | 7.4474 | 7.4136 | 7.3894 | 7.4113 | 25 | 7.1204 | 7.264 | 7.4142 | 7.5734 | 7.7356
Nyngan | 820/1:NYN | 66 | Nyngan Town ZS | Nevertire Tee | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Nyngan | 820:NVE | 66 | Nyngan 132/66kV STS | Nevertire ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/1 | 66 | Nyngan 132/66kV STS | Girilambone Tee | 28 | 15.0241 | 15.1576 | 15.2787 | 15.4072 | 15.5265 | 34 | 15.3692 | 15.4981 | 15.6745 | 15.8796 | 15.9643
Nyngan | 855/1a | 66 | Girilambone Tee | Girilambone ZS | 24 | 11.4117 | 11.4635 | 11.5011 | 11.5463 | 11.5849 | 29 | 11.8142 | 11.9739 | 12.1633 | 12.3321 | 12.4773
Nyngan | 855/2 | 66 | Girilambone Tee | Byrock Tee | 28 | 7.6427 | 7.78 | 7.9241 | 8.0608 | 8.1941 | 34 | 7.6568 | 7.6586 | 7.6765 | 7.7667 | 7.7003
Nyngan | 855/3 | 66 | Byrock Tee | Bourke ZS | 28 | 7.2937 | 7.4337 | 7.5835 | 7.7233 | 7.8593 | 34 | 7.3414 | 7.3447 | 7.3609 | 7.4526 | 7.3812
Nyngan | 855/3a | 66 | Byrock Tee | Byrock ZS | 15 | 0.11423 | 0.11515 | 0.11486 | 0.1148 | 0.11518 | 25 | 0.080336 | 0.080741 | 0.081023 | 0.081327 | 0.081537
Nyngan | 855/4 | 66 | Girilambone ZS | Tritton Mine ZS | 24 | 9.8976 | 9.933 | 9.9787 | 10.0162 | 10.0545 | 29 | 10.2545 | 10.3811 | 10.5491 | 10.6928 | 10.8215
Oberon | 94C | 132 | TransGrid Wallerawang 330/132/66kV STS | Oberon 132 ZS | 128 | 32.1088 | 33.0127 | 33.918 | 34.9009 | 35.8823 | 143 | 34.7506 | 35.4008 | 36.18 | 36.8098 | 37.7263
Oberon | 856 | 66 | TransGrid Wallerawang 330/132/66kV STS | Oberon Town ZS | 28 | 5.5639 | 5.6649 | 5.7625 | 5.8871 | 5.9996 | 32 | 6.4389 | 6.4516 | 6.4494 | 6.473 | 6.4837
Oberon | 81B | 33 | Oberon Town ZS | Burraga ZS | 8 | 0.44998 | 0.44812 | 0.44867 | 0.45011 | 0.45092 | 13 | 0.5195 | 0.51899 | 0.52093 | 0.52235 | 0.52354
Orange | 94G | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 85.4794 | 101.7972 | 114.7849 | 116.4729 | 121.922 | 142 | 100.8131 | 105.6884 | 116.1149 | 118.4878 | 124.2282
Orange | 9MC | 132 | TransGrid Orange North 132kV Sw Stn | Flyers Creek Sw Stn | 142 | 85.4794 | 101.7972 | 114.7849 | 116.4729 | 121.922 | 142 | 100.8131 | 105.6884 | 116.1149 | 118.4878 | 124.2282
Orange | 9MR | 132 | Flyers Creek Sw Stn | Cadia ZS | 180 | 119.6712 | 142.5161 | 160.6989 | 163.0621 | 170.6909 | 202 | 141.1384 | 147.9637 | 162.5609 | 165.883 | 173.9195
Orange | 807 | 66 | TransGrid Orange 132/66kV STS | Orange West & South Tee | 61 | 12.5645 | 12.5019 | 12.4672 | 12.3417 | 12.3214 | 68 | 14.7459 | 14.8442 | 14.993 | 15.0771 | 15.3123
Orange | 807/2 | 66 | Orange West & South Tee | Orange South ZS | 63 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0
Orange | 807/3 | 66 | Orange West & South Tee | Orange West ZS | 62 | 12.5645 | 12.5019 | 12.4672 | 12.3417 | 12.3214 | 69 | 14.7459 | 14.8442 | 14.993 | 15.0771 | 15.3123
Orange | 818/1 | 66 | TransGrid Orange 132/66kV STS | Blayney ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Orange | 8C2 | 66 | TransGrid Orange 132/66kV STS | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Orange | 8F1 | 66 | TransGrid Orange 132/66kV STS | Orange South ZS | 63 | 18.6612 | 19.0412 | 19.5582 | 20.022 | 20.6005 | 70 | 24.6869 | 24.9507 | 25.2151 | 25.4821 | 25.8021
Orange | 8M1 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 11 | 10.3231 | 10.3642 | 10.4718 | 10.642 | 10.6638 | 19 | 12.2272 | 12.3424 | 12.5139 | 12.6219 | 12.7695
Orange | 8M2 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 21 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Parkes | 300 | 132 | TransGrid Parkes 132/66kV STS | North Parkes Mine ZS | 87 | 33.7936 | 45.9808 | 54.6666 | 67.2466 | 74.0534 | 108 | 34.777 | 50.2623 | 58.9651 | 71.5983 | 78.4656
Parkes | 898 | 66 | TransGrid Parkes 132/66kV STS | Trundle ZS | 10 | 6.7882 | 6.7882 | 6.7882 | 6.7882 | 6.7882 | 16 | 6.364 | 6.364 | 6.364 | 6.364 | 6.364
Parkes | 899 | 66 | Parkes Town ZS | Peak Hill ZS | 12 | 10.3554 | 10.9259 | 11.4945 | 12.0538 | 12.6434 | 19 | 10.4067 | 10.4693 | 10.5329 | 10.6625 | 10.732
Parkes | 89G | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 61 | 14.4917 | 14.8185 | 15.1373 | 15.4446 | 15.7614 | 68 | 13.8535 | 13.9811 | 14.0831 | 14.2543 | 14.352
Parkes | 89L | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 39 | 13.0426 | 13.3366 | 13.6236 | 13.9001 | 14.1853 | 43 | 12.4682 | 12.583 | 12.6748 | 12.8289 | 12.9168
Parkes | 89M | 66 | Peak Hill ZS | Tomingley Mine ZS | 32 | 9.0949 | 9.6791 | 10.2581 | 10.8268 | 11.4273 | 40 | 9.3168 | 9.3923 | 9.4661 | 9.6103 | 9.6911
Tamworth | 801 | 66 | Transgrid Tamworth 132/66kV STS | Oxley Vale ZS | 63 | 14.5073 | 14.6489 | 14.8327 | 14.9603 | 15.2039 | 70 | 14.305 | 14.601 | 14.8564 | 15.1524 | 15.4199
Tamworth | 803 | 66 | Transgrid Tamworth 132/66kV STS | South Tamworth ZS | 70 | 28.2155 | 28.2379 | 28.288 | 28.2726 | 28.3691 | 78 | 28.1929 | 28.45 | 28.6679 | 28.9729 | 29.1891
Tamworth | 804 | 66 | Transgrid Tamworth 132/66kV STS | Nundle ZS | 8 | 1.4718 | 1.4547 | 1.4286 | 1.4163 | 1.4016 | 13 | 1.6908 | 1.711 | 1.7345 | 1.7629 | 1.7878
Tamworth | 806 | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 38 | 11.87 | 11.8757 | 16.2712 | 17.2331 | 18.0786 | 47 | 10.0119 | 13.9984 | 14.7083 | 15.7879 | 16.7236
Tamworth | 873 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 15.1741 | 15.1634 | 15.1736 | 15.1408 | 15.2441 | 61 | 13.2204 | 13.2733 | 13.2781 | 13.3466 | 13.355
Tamworth | 874 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 15.7934 | 15.7823 | 15.7929 | 15.7588 | 15.8663 | 61 | 13.76 | 13.8151 | 13.8201 | 13.8913 | 13.9001
Tamworth | 803/2 | 66 | South Tamworth ZS | Oxley Vale ZS | 63 | 4.8358 | 4.883 | 4.9442 | 4.9868 | 5.068 | 70 | 4.7683 | 4.867 | 4.9521 | 5.0508 | 5.14
Tamworth | 806/1 | 66 | Goddard Lane ZS | Attunga ZS | 18 | 11.0702 | 11.0655 | 11.0647 | 11.032 | 11.0314 | 33 | 8.5921 | 8.6332 | 8.6735 | 8.7071 | 8.7393
Tamworth | 806/2 | 66 | Attunga ZS | Manilla ZS | 18 | 7.6397 | 7.6341 | 7.6213 | 7.6049 | 7.5912 | 33 | 6.2357 | 6.2755 | 6.3123 | 6.3447 | 6.377
Tamworth | 806/3 | 66 | Manilla ZS | Upper Manilla ZS | 18 | 2.6607 | 2.6431 | 2.6347 | 2.6269 | 2.6174 | 33 | 2.5221 | 2.5362 | 2.5441 | 2.5586 | 2.5691
Tamworth | 806/4 | 66 | Upper Manilla ZS | Barraba ZS | 15 | 2.2759 | 2.2663 | 2.272 | 2.2767 | 2.277 | 25 | 2.3116 | 2.3252 | 2.335 | 2.3519 | 2.3627
Tamworth | 80C | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 61 | 10.5262 | 10.5312 | 14.4292 | 15.2822 | 16.0319 | 68 | 8.8785 | 12.4137 | 13.0432 | 14.0006 | 14.8304
Tamworth | 813:CLA | 66 | Transgrid Tamworth 132/66kV STS | Currububula ZS | 28 | 14.8768 | 14.8514 | 14.8238 | 14.8259 | 14.8442 | 34 | 13.4461 | 13.6579 | 13.8827 | 14.1234 | 14.3459
Tamworth | 813/1:QDI | 66 | Currububula ZS | Werris Creek ZS | 28 | 13.6208 | 13.602 | 13.5902 | 13.6016 | 13.6374 | 34 | 12.3962 | 12.5973 | 12.8116 | 13.0405 | 13.2513
Tamworth | 813/2:QDI | 66 | Werris Creek ZS | Quirindi ZS | 28 | 11.5137 | 11.5104 | 11.5122 | 11.5332 | 11.5847 | 34 | 10.5618 | 10.7771 | 11.0003 | 11.2363 | 11.4538
Tamworth | 870/1:KTL | 66 | Transgrid Tamworth 132/66kV STS | Kootingal Tee | 14 | 6.7402 | 6.7931 | 6.8319 | 6.8928 | 6.9515 | 21 | 6.4754 | 6.5668 | 6.6738 | 6.7932 | 6.908
Tamworth | 870/2:KTL | 66 | Kootingal Tee | Kootingal ZS | 12 | 6.0536 | 6.1025 | 6.1392 | 6.1952 | 6.2462 | 20 | 5.7441 | 5.8309 | 5.9336 | 6.0493 | 6.1602
Tamworth | 870/3:KTL | 66 | Kootingal Tee | Bendemeer ZS | 13 | 0.70044 | 0.7039 | 0.70603 | 0.71028 | 0.71775 | 21 | 0.73563 | 0.73979 | 0.74337 | 0.74645 | 0.75015
Tamworth | 798 | 33 | Quirindi ZS | Murrurundi ZS | 4 | 2.774 | 2.7752 | 2.7891 | 2.791 | 2.7835 | 6 | 2.5873 | 2.6343 | 2.6825 | 2.7305 | 2.7793
Tamworth | 799/1 | 33 | Quirindi ZS | Caroona Tee | 6 | 3.1068 | 3.1218 | 3.1346 | 3.1468 | 3.1642 | 10 | 2.5391 | 2.5471 | 2.5522 | 2.5557 | 2.5601
Tamworth | 799/2 | 33 | Caroona Tee | Caroona ZS | 4 | 0.96381 | 0.96173 | 0.96265 | 0.96066 | 0.96278 | 6 | 0.67723 | 0.68055 | 0.68456 | 0.68757 | 0.69108
Tamworth | 799/3 | 33 | Caroona Tee | Spring Ridge ZS | 3 | 0.6407 | 0.64663 | 0.65347 | 0.65858 | 0.66833 | 5 | 0.64494 | 0.64753 | 0.64918 | 0.65055 | 0.65166
Tamworth | 799/4 | 33 | Spring Ridge ZS | Colly Blue ZS | 3 | 1.2561 | 1.2705 | 1.279 | 1.2919 | 1.3015 | 5 | 0.97465 | 0.97645 | 0.97595 | 0.97521 | 0.97529
Wellington | 945/3 | 132 | TransGrid Line 945 Wellington 132kV Tee | Wellington 132kV ZS | 124 | 8.9765 | 8.9468 | 8.9824 | 9.0115 | 9.0151 | 139 | 9.1141 | 9.2419 | 9.3398 | 9.4103 | 9.5305
Wellington | 947/1 | 132 | TransGrid Line 947 Burrendong Tee | Burrendong Hydro | 36 | 6.6366 | 6.6296 | 6.6268 | 6.6415 | 6.6283 | 64 | 9.0136 | 9.0506 | 9.1278 | 9.2113 | 9.3571
Wellington | 94F | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 87.2404 | 87.7154 | 110.8576 | 145.2017 | 157.3293 | 194 | 83.5072 | 106.1088 | 140.25 | 152.3786 | 152.6962
Wellington | 94J | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 80.8528 | 81.2931 | 82.0109 | 93.1269 | 104.3722 | 194 | 78.3385 | 78.579 | 89.619 | 100.9869 | 101.2844
Wellington | 805 | 66 | Wellington 132kV ZS | Mumbil ZS | 11 | 1.3653 | 1.3715 | 1.3972 | 1.4123 | 1.4323 | 19 | 1.1216 | 1.1224 | 1.1237 | 1.1235 | 1.1195
Wellington | 813:WGN | 66 | Wellington 132kV ZS | Geurie Tee | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Albury | 997/1 | 132 | Union Rd ZS | Corowa ZS | 128 | 71.1282 | 70.3532 | 70.7632 | 72.051 | 71.8554 | 143 | 78.8673 | 78.6264 | 78.0264 | 78.4149 | 79.2802
Albury | 997/2 | 132 | Corowa ZS | Mulwala ZS | 128 | 82.4351 | 81.6988 | 82.1881 | 83.6059 | 83.4892 | 143 | 89.1767 | 88.9988 | 88.377 | 88.7727 | 89.6791
Albury | 99E | 132 | Union Rd ZS | Jelbart ZS | 148 | 18.5475 | 18.4379 | 18.3463 | 18.3424 | 18.2703 | 164 | 17.3048 | 17.5078 | 17.7701 | 17.9735 | 18.2145
Albury | 99G | 132 | Union Rd ZS | Jelbart ZS | 148 | 18.5475 | 18.4379 | 18.3463 | 18.3424 | 18.2703 | 164 | 17.3048 | 17.5078 | 17.7701 | 17.9735 | 18.2145
Bega | 84G | 66 | Bega 132/66kV STS | Eden South ZS | 61 | 6.7579 | 6.7484 | 6.7346 | 6.7256 | 6.719 | 68 | 8.0225 | 8.1004 | 8.1751 | 8.2599 | 8.3332
Bega | 84H | 66 | Eden South ZS | Edrom ZS | 38 | 2.3464 | 2.3518 | 2.3489 | 2.3652 | 2.3701 | 43 | 2.2695 | 2.2649 | 2.2537 | 2.2504 | 2.2426
Bega | 84M | 66 | Bega 132/66kV STS | Maher St ZS | 61 | 9.2522 | 9.2815 | 9.2882 | 9.3236 | 9.3599 | 68 | 11.5491 | 11.7479 | 11.9546 | 12.1313 | 12.3418
Bega | 89A | 66 | Bega 132/66 | Pambula ZS | 38 | 10.3949 | 10.3814 | 10.379 | 10.3524 | 10.3444 | 43 | 15.4994 | 15.5982 | 15.7217 | 15.8135 | 15.9069
Bega | 84P | 66 | Bega 132/66kV STS | Maher St ZS | 38 | 9.2522 | 9.2815 | 9.2882 | 9.3236 | 9.3599 | 43 | 11.5491 | 11.7479 | 11.9546 | 12.1313 | 12.3418
Bega | 89F | 66 | Pambula ZS | Eden South ZS | 30 | 2.6209 | 2.6167 | 2.6101 | 2.6071 | 2.6043 | 36 | 2.9449 | 2.975 | 3.0025 | 3.0366 | 3.0653
Bega | 84R/1 | 66 | Maher St ZS | Quira ZS | 6 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0
Bega | 7802/1 | 33 | Maher St ZS | Brogo ZS | 12 | 4.3037 | 4.3183 | 4.3243 | 4.3475 | 4.3705 | 24 | 6.2594 | 6.4581 | 6.6706 | 6.8537 | 7.0725
Bega | 7802/2 | 33 | Brogo ZS | Cobargo ZS | 10 | 3.8192 | 3.8222 | 3.8196 | 3.8297 | 3.8312 | 19 | 5.1787 | 5.2463 | 5.3325 | 5.4222 | 5.4994
Bega | 7814 | 33 | Cobargo ZS | Bermagui ZS | 5 | 2.6225 | 2.6259 | 2.6278 | 2.6295 | 2.6312 | 9 | 3.4477 | 3.4881 | 3.5511 | 3.6009 | 3.6623
Buronga | 87G | 66 | Dareton ZS | Ellerslie ZS | 67 | 8.2898 | 8.2915 | 8.3322 | 8.3431 | 8.3213 | 78 | 6.8775 | 6.8726 | 6.9088 | 6.91 | 6.9458
Buronga | 87H/1 | 66 | Ellerslie ZS | Ginkgo Snapper Tee | 45 | 6.6763 | 6.6661 | 6.7244 | 6.7286 | 6.7272 | 56 | 6.384 | 6.3787 | 6.4178 | 6.4121 | 6.4449
Buronga | 87H/2 | 66 | Ginkgo Snapper Tee | Ginkgo ZS | 20 | 6.6865 | 6.7006 | 6.737 | 6.7507 | 6.7473 | 39 | 6.7728 | 6.7755 | 6.8108 | 6.8069 | 6.8354
Buronga | 87H/3 | 66 | Ginkgo Snapper Tee | Snapper ZS | 12 | 0.2805 | 0.25406 | 0.28007 | 0.26961 | 0.2727 | 19 | 0.33653 | 0.3277 | 0.33918 | 0.3365 | 0.34467
Buronga | 83U | 66 | Powercor Mildura ZS (NSW Border) | Buronga ZS | 22 | 21.9689 | 22.8656 | 22.9167 | 23.5771 | 24.4602 | 43 | 17.1942 | 17.2281 | 17.3179 | 17.3109 | 17.1969
Buronga | 83W | 66 | Buronga ZS | Dareton ZS | 22 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0
Buronga | Merbein - Dareton Line | 66 | Powercor Mildura ZS (NSW Border) | Dareton ZS | 49 | 10.8784 | 10.7691 | 10.6631 | 10.6926 | 10.8091 | 61 | 9.588 | 9.7384 | 9.7001 | 9.6795 | 9.7145
Coleambally | CLY1526/1 | 33 | Coleambally 132/33kV STS | Coleambally Tee | 10 | 1.8661 | 1.8462 | 1.8311 | 1.8277 | 1.8224 | 19 | 1.8213 | 1.8244 | 1.8274 | 1.8308 | 1.8105
Coleambally | CLY1526/2 | 33 | Coleambally Tee | Coleambally ZS | 10 | 1.6965 | 1.6784 | 1.6646 | 1.6615 | 1.6567 | 19 | 1.6558 | 1.6586 | 1.6613 | 1.6643 | 1.6459
Coleambally | CLY1526/3 | 33 | Coleambally Tee | Egansford ZS | 8 | 0.98199 | 0.97381 | 0.94636 | 0.93452 | 0.92548 | 13 | 0.9938 | 1.0072 | 0.99804 | 1.0201 | 1.0318
Coleambally | CLY1530/1 | 33 | Coleambally 132/33kV STS | Ringwood Rd ZS | 8 | 5.2025 | 5.1738 | 5.1597 | 5.1575 | 5.1456 | 13 | 4.0915 | 4.1358 | 4.1837 | 4.233 | 4.2658
Coleambally | CLY1530/2 | 33 | Ringwood Rd ZS | Darlington Point ZS | 8 | 3.4328 | 3.416 | 3.4145 | 3.418 | 3.4184 | 13 | 2.7977 | 2.8837 | 2.9501 | 3.0282 | 3.0916
Cooma | 974 | 132 | TransGrid Cooma 132/66kV STS | Bega 132/66kV STS | 128 | 15.9432 | 15.9079 | 15.9723 | 15.9173 | 15.8763 | 143 | 22.7252 | 22.7494 | 22.6486 | 22.7743 | 22.7525
Cooma | 97R/1 | 132 | TransGrid Cooma 132/66kV STS | Steeple Flat 132/66kV STS | 140 | 86.8929 | 87.0044 | 86.9806 | 87.0725 | 86.8943 | 157 | 72.4959 | 73.0774 | 72.2917 | 72.1465 | 72.5348
Cooma | 82D | 66 | TransGrid Cooma 132/66kV STS | Jindabyne East ZS | 20 | 4.7606 | 4.8126 | 4.8603 | 4.9127 | 4.9689 | 39 | 11.4296 | 11.6244 | 11.7771 | 11.9787 | 12.1585
Cooma | 84J | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 70 | 5.1424 | 5.1383 | 5.1319 | 5.1302 | 5.1301 | 78 | 6.973 | 7.0591 | 7.1576 | 7.2416 | 7.346
Cooma | 84L | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 64 | 5.1424 | 5.1383 | 5.1319 | 5.1302 | 5.1301 | 71 | 6.973 | 7.0591 | 7.1576 | 7.2416 | 7.346
Cooma | 82J/1 | 66 | Snowy Adit 132/66/11kV ZS | Snowy Lookout Sw Stn | 12 | 3.9712 | 3.977 | 3.9184 | 3.9171 | 3.8824 | 20 | 7.7737 | 8.0337 | 8.2454 | 8.4683 | 8.7055
Cooma | 82J/2 | 66 | Jindabyne ZS | Snowy Lookout Sw Stn | 12 | 3.8678 | 3.8749 | 3.8155 | 3.8142 | 3.7796 | 19 | 7.2886 | 7.5474 | 7.7602 | 7.9815 | 8.2166
Cooma | 82R | 66 | Jindabyne East ZS | Jindabyne ZS | 20 | 2.2683 | 2.2678 | 2.2635 | 2.2676 | 2.2636 | 39 | 6.1302 | 6.2204 | 6.2818 | 6.3693 | 6.43
Cooma | 888/1 | 66 | TransGrid Cooma 132/66kV STS | Rhine Falls Sw Stn | 16 | 1.5315 | 1.5482 | 1.5652 | 1.577 | 1.5979 | 25 | 2.1921 | 2.1919 | 2.1951 | 2.2114 | 2.2014
Cooma | 888/3 | 66 | Rhine Falls Sw Stn | Adaminaby ZS | 16 | 1.1642 | 1.1822 | 1.2007 | 1.2136 | 1.2355 | 25 | 1.7257 | 1.723 | 1.7232 | 1.7359 | 1.7232
Cooma | 888/4 | 66 | Rhine Falls Sw Stn | Eucumbene Tee | 15 | 0.27186 | 0.27182 | 0.27216 | 0.27182 | 0.27234 | 25 | 0.37106 | 0.37457 | 0.37833 | 0.38311 | 0.38704
Cooma | 888/6 | 66 | Eucumbene Tee | Eucumbene ZS | 15 | 0.13884 | 0.13873 | 0.1389 | 0.13861 | 0.13891 | 25 | 0.24086 | 0.24428 | 0.24818 | 0.25295 | 0.25667
Cooma | 888/7 | 66 | Eucumbene Tee | Snowy Adit 132/66/11kV ZS | 20 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Cooma | 849/1 | 33 | Adaminaby ZS | Providence Portal ZS | 7 | 0.088684 | 0.089341 | 0.090666 | 0.088573 | 0.090103 | 12 | 0.26578 | 0.26043 | 0.26525 | 0.27543 | 0.26628
Cowra | 865 | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 9.6134 | 9.6308 | 9.645 | 9.7102 | 9.7251 | 25 | 7.9806 | 8.0473 | 8.1156 | 8.1855 | 8.2677
Cowra | 863:CWD | 66 | TransGrid Cowra 132/66kV STS | Canowindra ZS | 9 | 5.8609 | 5.8805 | 5.8777 | 5.8966 | 5.9428 | 15 | 5.0165 | 5.0651 | 5.1092 | 5.1531 | 5.2017
Cowra | 866:COW | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 9.6134 | 9.6308 | 9.645 | 9.7102 | 9.7251 | 25 | 7.9806 | 8.0473 | 8.1156 | 8.1855 | 8.2677
Cowra | 891/1 | 66 | TransGrid Cowra 132/66kV STS | Wyangala Dam Tee | 20 | 30.7549 | 30.7614 | 30.7696 | 30.7802 | 30.7847 | 24 | 31.0679 | 31.0667 | 31.0646 | 31.072 | 31.0706
Cowra | 891/2 | 66 | Wyangala Dam Tee | Wyangala Dam | 19 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 33 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 31.8198
Cowra | 891/5 | 66 | Monteagle Tee | Monteagle ZS | 13 | 0.86287 | 0.86075 | 0.85825 | 0.8529 | 0.84893 | 22 | 0.91892 | 0.92238 | 0.92655 | 0.93216 | 0.93725
Cowra | 891/6 | 66 | Monteagle Tee | Young ZS | 19 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0
Cowra | 891/7 | 66 | Bendick Murrell Tee | Bendick Murrell ZS | 19 | 1.7044 | 1.7168 | 1.7225 | 1.729 | 1.7452 | 33 | 1.538 | 1.5444 | 1.5502 | 1.548 | 1.5553
Cowra | 891:BMU/1 | 66 | Wyangala Dam Tee | Bendick Murrell Tee | 19 | 2.4387 | 2.4485 | 2.4517 | 2.4528 | 2.4644 | 33 | 2.334 | 2.3426 | 2.351 | 2.3527 | 2.3618
Cowra | 891:BMU/2 | 66 | Bendick Murrell Tee | Monteagle Tee | 19 | 0.86287 | 0.86075 | 0.85825 | 0.8529 | 0.84893 | 33 | 0.91892 | 0.92238 | 0.92655 | 0.93216 | 0.93725
Cowra | 893/1 | 66 | TransGrid Cowra 132/66kV STS | Grenfell Tee | 12 | 4.4164 | 4.416 | 4.4087 | 4.4159 | 4.4126 | 18 | 4.7513 | 4.8023 | 4.8748 | 4.9334 | 5.028
Cowra | 893/4 | 66 | Grenfell Tee | Payten's Bridge ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Cowra | 893/6 | 66 | Grenfell Tee | Grenfell ZS | 12 | 4.4164 | 4.416 | 4.4087 | 4.4159 | 4.4126 | 18 | 4.7513 | 4.8023 | 4.8748 | 4.9334 | 5.028
Darlington Point | 99N | 132 | TransGrid Darlington Point 330/132kV STS | Hillston ZS | 128 | 13.3586 | 13.4261 | 13.4734 | 13.5621 | 13.5534 | 143 | 12.8945 | 13.1389 | 13.4113 | 13.6657 | 13.9176
Darlington Point | 99R | 132 | TransGrid Darlington Point 330/132kV STS | Hay 132 ZS | 128 | 10.2559 | 10.256 | 10.242 | 10.2618 | 10.2812 | 143 | 14.1996 | 14.2406 | 14.2568 | 14.2772 | 14.2892
Darlington Point | HAT 22 | 33 | Hay 132 ZS | Hay ZS | 8 | 4.5453 | 4.5709 | 4.6046 | 4.6284 | 4.657 | 14 | 7.0198 | 7.0517 | 7.0874 | 7.132 | 7.1697
Darlington Point | HAT 32 | 33 | Hay 132 ZS | Hay ZS | 8 | 1.1363 | 1.1427 | 1.1512 | 1.1571 | 1.1643 | 14 | 1.7549 | 1.7629 | 1.7719 | 1.783 | 1.7924
Darlington Point | HAT 42 | 33 | Hay 132 ZS | Carrathool ZS | 7 | 6.9162 | 6.9071 | 6.8867 | 6.8933 | 6.9048 | 12 | 7.3576 | 7.378 | 7.3878 | 7.3979 | 7.4055
Darlington Point | HIL1117 | 33 | Hillston ZS | Ivanhoe ZS | 8 | 5.5728 | 5.6388 | 5.672 | 5.7095 | 5.7416 | 14 | 4.1722 | 4.2059 | 4.2412 | 4.282 | 4.3276
Deniliquin | 844 | 66 | TransGrid Deniliquin 132/66kV STS | Barham ZS | 11 | 5.4977 | 5.5244 | 5.5714 | 5.6032 | 5.6298 | 19 | 4.939 | 4.9764 | 5.0179 | 5.0649 | 5.1143
Deniliquin | 845 | 66 | TransGrid Deniliquin 132/66kV STS | Deniliquin ZS | 38 | 20.9101 | 21.0118 | 21.1905 | 21.3115 | 21.4124 | 43 | 18.7604 | 18.9028 | 19.0601 | 19.2388 | 19.4266
Deniliquin | 822/1 | 66 | TransGrid Deniliquin 132/66kV STS | Murgha ZS | 11 | 7.1893 | 7.2243 | 7.2857 | 7.3273 | 7.362 | 19 | 7.0447 | 7.0982 | 7.1573 | 7.2244 | 7.2949
Deniliquin | 822/2 | 66 | Murgha ZS | Moulamein ZS | 11 | 6.0146 | 6.0438 | 6.0952 | 6.13 | 6.1591 | 19 | 6.011 | 6.0566 | 6.107 | 6.1643 | 6.2244
Deniliquin | 84Y | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 66 | 8.0821 | 8.1214 | 8.1905 | 8.2372 | 8.2763 | 66 | 4.7475 | 4.7836 | 4.8234 | 4.8686 | 4.9161
Deniliquin | MM61 | 66 | Moulamein ZS | Koraleigh ZS | 15 | 3.9941 | 4.0135 | 4.0476 | 4.0707 | 4.09 | 25 | 2.8332 | 2.8547 | 2.8785 | 2.9055 | 2.9338
Deniliquin | No.6 Moama | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 34 | 5.6387 | 5.6661 | 5.7143 | 5.7469 | 5.7741 | 39 | 3.3692 | 3.3948 | 3.423 | 3.4551 | 3.4889
Finley | 9R4 | 132 | TransGrid Finley 132/66kV STS | Mulwala ZS | 140 | 92.4897 | 91.7808 | 92.2714 | 93.7503 | 93.6597 | 157 | 97.5889 | 97.4912 | 96.9508 | 97.4374 | 98.4275
Finley | 84A | 66 | TransGrid Finley 132/66kV STS | Jerilderie ZS | 15 | 3.0243 | 3.0232 | 3.0359 | 3.0389 | 3.045 | 25 | 3.937 | 3.9579 | 3.9713 | 4.0031 | 4.0307
Finley | 84B | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 4.2389 | 4.2523 | 4.2525 | 4.2651 | 4.2735 | 70 | 3.981 | 4.0133 | 4.0404 | 4.0716 | 4.0947
Finley | 84C | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 7.8722 | 7.8972 | 7.8975 | 7.9208 | 7.9364 | 70 | 7.3933 | 7.4533 | 7.5036 | 7.5616 | 7.6044
Goulburn | 972 | 132 | TransGrid Marulan 330/132kV STS | Goulburn 132/66/33kV STS | 180 | 57.1068 | 55.8917 | 54.6971 | 54.2131 | 52.9067 | 202 | 52.6786 | 50.5146 | 48.5445 | 46.4938 | 44.4311
Goulburn | 9UR | 132 | TransGrid Marulan 330/132kV STS | Taralga Wind Farm | 140 | 103.8596 | 103.9987 | 104.0791 | 104.86 | 104.8381 | 157 | 109.9129 | 110.0671 | 110.4796 | 110.4618 | 110.6978
Goulburn | 843 | 66 | Clinton St ZS | Goulburn North ZS | 46 | 4.2884 | 4.3188 | 4.3501 | 4.4103 | 4.5042 | 52 | 5.453 | 5.5174 | 5.5898 | 5.6631 | 5.7526
Goulburn | 82K/2 | 66 | Woodlawn ZS | Bungendore ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Goulburn | 840:GOU | 66 | Goulburn 132/66/33kV STS | Goulburn North ZS | 61 | 7.3735 | 7.4047 | 7.3797 | 7.3191 | 7.3626 | 68 | 11.0016 | 11.0122 | 11.0144 | 11.0812 | 11.0634
Goulburn | 841:GBN | 66 | Goulburn North ZS | Crookwell ZS | 9 | 3.7908 | 3.7881 | 3.7953 | 3.8233 | 3.8269 | 13 | 4.346 | 4.3422 | 4.3248 | 4.3353 | 4.3492
Goulburn | 850:GOU | 66 | Goulburn 132/66/33kV STS | Woodlawn ZS | 28 | 7.81 | 7.8605 | 7.8631 | 7.8953 | 7.8648 | 34 | 7.2281 | 7.2278 | 7.2719 | 7.3413 | 7.3424
Goulburn | 86M/1 | 66 | Goulburn 132/66/33kV STS | Marulan North Tee | 25 | 12.4415 | 12.4771 | 12.5655 | 12.6023 | 12.7088 | 29 | 13.2402 | 13.4572 | 13.666 | 13.8757 | 14.0975
Goulburn | 86M/2 | 66 | Marulan North Tee | Marulan South ZS | 25 | 7.5415 | 7.5531 | 7.5855 | 7.5726 | 7.6071 | 29 | 7.6624 | 7.7208 | 7.7813 | 7.8356 | 7.912
Goulburn | 86L | 66 | Marulan North Tee | Marulan North ZS | 12 | 6.3289 | 6.352 | 6.4141 | 6.4644 | 6.5457 | 19 | 7.1237 | 7.3112 | 7.4832 | 7.6617 | 7.8329
Goulburn | 870:GOU | 66 | Goulburn 132/66/33kV STS | Clinton St ZS | 34 | 18.1958 | 18.2566 | 18.2554 | 18.2621 | 18.4729 | 41 | 24.8397 | 25.0102 | 25.1894 | 25.4424 | 25.6381
Goulburn | GOU12 | 33 | Goulburn 132/66/33kV STS | Brisbane Grove ZS | 7 | 2.353 | 2.3782 | 2.3845 | 2.397 | 2.4373 | 12 | 2.6592 | 2.6762 | 2.6962 | 2.7133 | 2.7315
Griffith | 79C/1 | 33 | TransGrid Griffith 132/33kV STS | Widgelli / Willbriggie Tee | 10 | 6.2285 | 6.2115 | 6.2171 | 6.2103 | 6.2238 | 19 | 5.8942 | 6.0174 | 6.1418 | 6.2777 | 6.3925
Griffith | 79C/2 | 33 | Widgelli / Willbriggie Tee | Widgelli ZS | 10 | 1.2085 | 1.2052 | 1.2063 | 1.205 | 1.2076 | 19 | 1.014 | 1.0352 | 1.0567 | 1.08 | 1.0998
Griffith | 79C/3 | 33 | Widgelli / Willbriggie Tee | Willbriggie Tee | 10 | 5.02 | 5.0063 | 5.0108 | 5.0053 | 5.0162 | 19 | 4.8801 | 4.9821 | 5.0852 | 5.1977 | 5.2927
Griffith | 79C/4 | 33 | Willbriggie Tee | Willbriggie ZS | 10 | 4.4622 | 4.4501 | 4.4541 | 4.4492 | 4.4589 | 19 | 4.3097 | 4.3998 | 4.4908 | 4.5902 | 4.6741
Griffith | 79C/5 | 33 | Willbriggie Tee | 79C / 79P Tee | 10 | 0.55777 | 0.55626 | 0.55676 | 0.55615 | 0.55736 | 19 | 0.50702 | 0.51762 | 0.52833 | 0.54002 | 0.54989
Griffith | 79F | 33 | TransGrid Griffith 132/33kV STS | Yenda ZS | 22 | 12.178 | 12.145 | 12.1559 | 12.1426 | 12.169 | 27 | 8.6828 | 8.8643 | 9.0476 | 9.2478 | 9.4169
Griffith | 79G | 33 | Beelbangera ZS | Griffith ZS | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0
Griffith | 79J | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0
Griffith | 79L | 33 | TransGrid Griffith 132/33kV STS | Beelbangera ZS | 10 | 13.5725 | 13.5356 | 13.5477 | 13.5329 | 13.5624 | 19 | 8.2391 | 8.4114 | 8.5853 | 8.7753 | 8.9357
Griffith | 79M | 33 | TransGrid Griffith 132/33kV STS | Hanwood ZS | 22 | 14.0423 | 14.0718 | 14.1092 | 14.1691 | 14.1633 | 27 | 12.4228 | 12.5425 | 12.5986 | 12.8278 | 12.9382
Griffith | 79P | 33 | TransGrid Griffith 132/33kV STS | Warrawidgee Tee | 22 | 9.5751 | 9.5491 | 9.5577 | 9.5472 | 9.568 | 27 | 7.7321 | 7.8938 | 8.057 | 8.2353 | 8.3858
Griffith | 79W/1 | 33 | Warrawidgee Tee | Warrawidgee ZS | 6 | 2.2311 | 2.225 | 2.227 | 2.2246 | 2.2294 | 9 | 1.7746 | 1.8117 | 1.8491 | 1.8901 | 1.9246
Griffith | 79W/2 | 33 | Warrawidgee Tee | Nericon Tee | 21 | 6.6933 | 6.6751 | 6.6811 | 6.6738 | 6.6883 | 27 | 5.4505 | 5.5645 | 5.6795 | 5.8052 | 5.9113
Griffith | 79W/3 | 33 | Nericon Tee | Nericon ZS | 20 | 2.9748 | 2.9667 | 2.9694 | 2.9661 | 2.9726 | 23 | 1.9013 | 1.9411 | 1.9812 | 2.0251 | 2.0621
Griffith | 79R | 33 | TransGrid Griffith 132/33kV STS | Tharbogang ZS | 31 | 13.6659 | 13.7261 | 13.7847 | 13.7914 | 13.893 | 34 | 10.2534 | 10.3216 | 10.3707 | 10.4514 | 10.5068
Griffith | 79U | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 23.5403 | 23.5123 | 23.5301 | 23.5067 | 23.6067 | 56 | 20.6529 | 20.6733 | 20.7233 | 20.6587 | 20.7272
Harden - Murrumburrah | 836 | 66 | TransGrid Murrumburrah 132/66kV STS | Cootamundra ZS | 20 | 9.3233 | 9.2891 | 9.2767 | 9.2705 | 9.3691 | 24 | 8.7106 | 8.7848 | 8.8501 | 8.9249 | 9.0017
Harden - Murrumburrah | 837 | 66 | TransGrid Murrumburrah 132/66kV STS | Jugiong ZS | 12 | 1.6656 | 1.6818 | 3.3998 | 3.4171 | 3.4371 | 18 | 1.4802 | 1.4696 | 3.1799 | 3.1706 | 3.1605
Harden - Murrumburrah | 847 | 66 | TransGrid Murrumburrah 132/66kV STS | Boorowa ZS | 10 | 6.0138 | 6.0092 | 6.0002 | 5.9999 | 6.0011 | 16 | 6.5026 | 6.6295 | 6.7544 | 6.8918 | 7.0056
Harden - Murrumburrah | 823/3 | 66 | Bogalara Sw Stn | Marilba ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 830/1:PCR | 66 | Bogalara Sw Stn | Parsons Creek ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 838/3 | 66 | Jugiong ZS | Bogalara Sw Stn | 12 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 83A | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 4.4161 | 4.3701 | 4.3579 | 4.3555 | 4.3469 | 25 | 4.8747 | 4.9071 | 4.9584 | 4.99 | 5.0329
Harden - Murrumburrah | 83D | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 890:YOU | 66 | TransGrid Murrumburrah 132/66kV STS | Young ZS | 24 | 15.9571 | 15.8835 | 15.9356 | 15.9376 | 15.893 | 28 | 18.0718 | 18.2802 | 18.5433 | 18.7371 | 18.9913
Moruya North | 98H | 132 | Endeavour Energy Evans Lane Sw Stn | Moruya North 132/33kV STS | 180 | 21.7342 | 21.8145 | 21.8819 | 21.9524 | 22.051 | 202 | 26.0387 | 26.2804 | 26.4812 | 26.7474 | 26.9505
Moruya North | 98M | 132 | Endeavour Energy Evans Lane Sw Stn | Batemans Bay ZS | 50 | 19.2264 | 19.2974 | 19.357 | 19.4194 | 19.5067 | 62 | 23.0343 | 23.2481 | 23.4256 | 23.6611 | 23.8408
Moruya North | 98T | 132 | Batemans Bay ZS | Moruya North 132/33kV STS | 61 | 4.1796 | 4.1951 | 4.2081 | 4.2216 | 4.2406 | 70 | 5.0075 | 5.0539 | 5.0925 | 5.1437 | 5.1828
Moruya North | 7703 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 30 | 6.5129 | 6.5192 | 6.5058 | 6.5157 | 6.5507 | 34 | 8.7333 | 8.8291 | 8.9292 | 9.0365 | 9.1354
Moruya North | 7704 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 26 | 8.3304 | 8.3385 | 8.3213 | 8.334 | 8.3788 | 30 | 11.1705 | 11.293 | 11.4211 | 11.5583 | 11.6849
Moruya North | 7706 | 33 | Moruya North 132/33kV STS | Mossy Point ZS | 25 | 7.0818 | 7.1859 | 7.2366 | 7.3169 | 7.3617 | 28 | 9.524 | 9.6314 | 9.6872 | 9.8278 | 9.9024
Moruya North | 7712 | 33 | Bodalla Tee | Bodalla ZS | 10 | 1.2409 | 1.236 | 1.2308 | 1.2299 | 1.2329 | 19 | 1.5151 | 1.5227 | 1.5343 | 1.5369 | 1.5516
Moruya North | 7713 | 33 | Bodalla Tee | Narooma ZS | 21 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0
Moruya North | 7817 | 33 | Narooma Tee | Cobargo ZS | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/1 | 33 | Moruya Town ZS | Tuross Tee | 17 | 3.0069 | 2.9912 | 2.9663 | 2.9579 | 2.9622 | 19 | 4.2013 | 4.2596 | 4.3061 | 4.3714 | 4.4314
Moruya North | 7711/2 | 33 | Tuross Tee | Tuross ZS | 7 | 2.0837 | 2.0706 | 2.0478 | 2.0394 | 2.0415 | 12 | 2.8963 | 2.9499 | 2.9873 | 3.0534 | 3.1019
Moruya North | 7711/3 | 33 | Tuross Tee | Bodalla Tee | 21 | 1.2764 | 1.2713 | 1.266 | 1.2651 | 1.2681 | 27 | 1.5584 | 1.5662 | 1.5782 | 1.5808 | 1.596
Moruya North | 7715/1 | 33 | Moruya Town ZS | Narooma Tee | 30 | 6.5579 | 6.5849 | 6.6017 | 6.6294 | 6.6778 | 34 | 9.1901 | 9.2627 | 9.3632 | 9.4306 | 9.5012
Moruya North | 7715/2 | 33 | Narooma Tee | Narooma ZS | 10 | 6.2598 | 6.2855 | 6.3016 | 6.3281 | 6.3743 | 19 | 8.7723 | 8.8417 | 8.9376 | 9.0019 | 9.0693
Morven | 996/1 | 132 | TransGrid 132kV Line 996 Tee | Morven 132/66kV STS | 45 | 7.421 | 7.544 | 7.6327 | 7.7642 | 7.8354 | 86 | 7.7692 | 7.8267 | 7.8838 | 7.9128 | 7.9808
Morven | 83M/3 | 66 | Morven 132/66kV STS | Culcairn ZS | 15 | 3.7923 | 3.7968 | 3.8073 | 3.8097 | 3.816 | 25 | 4.4631 | 4.4996 | 4.5191 | 4.5411 | 4.5699
Morven | 83M/4 | 66 | Morven 132/66kV STS | Holbrook ZS | 15 | 3.4524 | 3.4557 | 3.4559 | 3.4499 | 3.4595 | 25 | 3.3115 | 3.3096 | 3.3186 | 3.3274 | 3.3278
Munyang | 56 | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 2.5318 | 2.5507 | 2.5796 | 2.5965 | 2.6297 | 23 | 15.7365 | 15.7901 | 15.8092 | 15.818 | 15.8388
Munyang | 57A | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.75237 | 0.77121 | 0.78537 | 0.79157 | 0.80466 | 23 | 5.508 | 5.5369 | 5.5857 | 5.6311 | 5.6569
Munyang | 57B | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.50158 | 0.51414 | 0.52358 | 0.52771 | 0.53644 | 23 | 3.672 | 3.6912 | 3.7238 | 3.7541 | 3.7712
Munyang | No.1 Perisher | 33 | TransGrid Munyang 132/33kV STS | Smiggin Sw Stn | 38 | 2.5318 | 2.5507 | 2.5796 | 2.5965 | 2.6297 | 41 | 15.7365 | 15.7901 | 15.8092 | 15.818 | 15.8388
Munyang | No.2 Perisher/1 | 33 | TransGrid Munyang 132/33kV STS | Blue Cow Tee | 38 | 1.7404 | 1.7806 | 1.8181 | 1.8249 | 1.8385 | 49 | 14.4105 | 14.4942 | 14.5383 | 14.6232 | 14.6358
Munyang | No.2 Perisher/2 | 33 | Blue Cow Tee | Smiggin Sw Stn | 38 | 1.2539 | 1.2854 | 1.309 | 1.3193 | 1.3411 | 49 | 9.18 | 9.2281 | 9.3094 | 9.3852 | 9.4281
Munyang | 60/2 | 33 | Bullocks Portal ZS | Bullocks Flat ZS | 19 | 2.2153 | 2.2319 | 2.2571 | 2.2719 | 2.301 | 23 | 15.7365 | 15.7901 | 15.8092 | 15.818 | 15.8388
Munyang | 58 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.70711 | 0.70711 | 0.70711 | 0.70711 | 0.70711 | 14 | 14.1421 | 14.1421 | 14.1421 | 14.1421 | 14.1421
Munyang | 59 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 1.5288 | 1.5428 | 1.557 | 1.5698 | 1.587 | 14 | 6.803 | 6.8128 | 6.8103 | 6.7933 | 6.7854
Munyang | Bullocks Portal Line | 33 | Perisher ZS | Bullocks Portal ZS | 20 | 2.5318 | 2.5507 | 2.5796 | 2.5965 | 2.6297 | 23 | 15.7365 | 15.7901 | 15.8092 | 15.818 | 15.8388
Queanbeyan | 97Y | 132 | TransGrid Williamsdale 330/132kV STS | Googong Town ZS | 91 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 975 | 132 | TransGrid Queanbeyan 132/66kV STS | Googong Town ZS | 41 | 8.3324 | 8.5897 | 8.8222 | 9.0588 | 9.3601 | 79 | 13.071 | 13.6692 | 14.2212 | 14.8176 | 15.3888
Queanbeyan | 82A | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 9.8098 | 10.0139 | 13.3437 | 13.5996 | 13.6928 | 37 | 13.57 | 16.9033 | 17.0364 | 17.112 | 17.205
Queanbeyan | 82B | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 7.3574 | 7.5105 | 10.0078 | 10.1997 | 10.2696 | 37 | 10.1775 | 12.6775 | 12.7773 | 12.834 | 12.9038
Queanbeyan | 82F | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 49 | 12.4593 | 12.4093 | 12.846 | 12.8524 | 12.8558 | 49 | 18.8348 | 19.3207 | 19.3919 | 19.4755 | 19.5598
Queanbeyan | 82G | 66 | TransGrid Queanbeyan 132/66kV STS | Captains Flat ZS | 12 | 6.84 | 7.2371 | 7.5547 | 7.9346 | 8.2449 | 19 | 8.4321 | 8.855 | 9.1765 | 9.5617 | 9.8367
Queanbeyan | 82K | 66 | TransGrid Queanbeyan 132/66kV STS | Sutton / Bungendore Tee | 28 | 11.9665 | 12.0685 | 12.1223 | 12.1293 | 12.2054 | 34 | 15.6041 | 15.8968 | 16.2232 | 16.4869 | 16.8187
Queanbeyan | 82K/1 | 66 | Sutton / Bungendore Tee | Bungendore ZS | 28 | 8.1608 | 8.2579 | 8.2965 | 8.296 | 8.3482 | 34 | 10.2361 | 10.3677 | 10.5231 | 10.6348 | 10.7955
Queanbeyan | 82K/3 | 66 | Sutton / Bungendore Tee | Sutton ZS | 28 | 3.8185 | 3.8262 | 3.8438 | 3.8541 | 3.8812 | 34 | 5.3734 | 5.5353 | 5.7073 | 5.8604 | 6.0324
Queanbeyan | 82M | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 830:QSH | 66 | Queanbeyan South ZS | Googong Dam ZS | 15 | 0.95606 | 0.96314 | 0.96063 | 0.97023 | 0.97246 | 25 | 1.1298 | 1.1392 | 1.1356 | 1.1397 | 1.1559
Steeple Flat | 97C | 132 | Steeple Flat 132/66kV STS | Boco Rock Wind Farm | 140 | 114.9464 | 115.0351 | 115.0711 | 115.0825 | 114.8755 | 157 | 109.3314 | 109.9378 | 109.0453 | 109.0462 | 109.4069
Steeple Flat | 97R/2 | 132 | Steeple Flat 132/66kV STS | Bega 132/66kV STS | 140 | 16.3693 | 16.3331 | 16.3992 | 16.3427 | 16.3006 | 157 | 23.6032 | 23.6284 | 23.5237 | 23.6542 | 23.6316
Steeple Flat | 84R/5 | 66 | Steeple Flat 132/66kV STS | Brown Mountain Hydro | 70 | 4.3903 | 4.3855 | 4.3865 | 4.3961 | 4.3987 | 78 | 4.6985 | 4.7261 | 4.7124 | 4.7054 | 4.7202
Steeple Flat | 810/4 | 66 | Steeple Flat 132/66kV STS | Bombala ZS | 21 | 4.2675 | 4.2772 | 4.2817 | 4.2923 | 4.283 | 25 | 5.0424 | 5.0964 | 5.1446 | 5.196 | 5.248
Steeple Flat | 84R/3 | 66 | Brown Mountain Hydro | Quira ZS | 70 | 1.1994 | 1.1994 | 1.2043 | 1.1936 | 1.1939 | 78 | 1.5659 | 1.5597 | 1.5558 | 1.5544 | 1.5635
Temora | 901 | 132 | Temora 132/66 STS | Wyalong Switching Station | 108 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0
Temora | 9JW | 132 | Wyalong Switching Station | West Wyalong Switching Station | 108 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0
Temora | 9JX | 132 | West Wyalong Switching Station | Lake Cowal | 108 | 35.6394 | 35.7453 | 35.6999 | 35.6751 | 35.6625 | 135 | 37.4528 | 37.362 | 37.5412 | 37.6171 | 37.6902
Temora | 4 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Temora | 5 | 66 | Temora 132/66 STS | Ariah Park Tee | 21 | 11.7299 | 11.9663 | 12.2161 | 12.5877 | 12.8886 | 25 | 12.4097 | 12.8915 | 13.2722 | 13.617 | 14.0399
Temora | 6 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 7.1271 | 7.099 | 7.111 | 7.0972 | 7.1469 | 25 | 6.9924 | 7.0776 | 7.1475 | 7.2364 | 7.3223
Temora | 20-60 | 66 | Ariah Park Tee | West Wyalong ZS | 21 | 9.7749 | 9.9719 | 10.18 | 10.4898 | 10.7405 | 25 | 10.3414 | 10.7429 | 11.0602 | 11.3475 | 11.6999
Temora | 60-70 | 66 | West Wyalong ZS | Anona ZS | 7 | 1.3191 | 1.3401 | 1.357 | 1.3738 | 1.3921 | 12 | 1.1656 | 1.1735 | 1.1775 | 1.1839 | 1.187
Temora | 80-140/1 | 66 | Ariah Park Tee | Ariah Park ZS | 15 | 1.955 | 1.9944 | 2.036 | 2.098 | 2.1481 | 25 | 2.0683 | 2.1486 | 2.212 | 2.2695 | 2.34
Temora | 80-140/2 | 66 | Ariah Park Tee | Ardlethan ZS | 11 | 0.77996 | 0.78052 | 0.77881 | 0.78321 | 0.78237 | 19 | 0.70961 | 0.71562 | 0.72026 | 0.72975 | 0.73251
Temora | 835/J | 66 | Junee Reefs ZS | Junee ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Temora | 835/T | 66 | Temora 132/66 STS | Junee Reefs ZS | 12 | 0.19465 | 0.19727 | 0.20041 | 0.20483 | 0.20915 | 18 | 0.21398 | 0.21562 | 0.21774 | 0.22028 | 0.22175
Tumut | 827 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 12.8521 | 12.7434 | 12.7114 | 12.6702 | 12.5417 | 34 | 13.8663 | 13.8128 | 13.9315 | 13.8765 | 13.8883
Tumut | 828 | 66 | TransGrid Tumut 132/66kV STS | Gundagai South ZS | 11 | 7.0714 | 7.0761 | 7.0799 | 7.0687 | 7.0895 | 19 | 6.7231 | 6.7878 | 6.8502 | 6.9093 | 6.9894
Tumut | 829 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Tumut | 831 | 66 | Gundagai South ZS | Nangus ZS | 11 | 1.1543 | 1.1458 | 1.1415 | 1.1325 | 1.129 | 19 | 0.93285 | 0.94173 | 0.94718 | 0.95916 | 0.96865
Tumut | 848 | 66 | Adelong Tee | Adelong ZS | 12 | 1.3628 | 1.3739 | 1.3662 | 1.3707 | 1.359 | 19 | 1.3053 | 1.3049 | 1.3091 | 1.3095 | 1.3134
Tumut | 830/2:GUN | 66 | Gundagai South ZS | Parsons Creek ZS | 11 | 0.21966 | 0.21847 | 0.21693 | 0.21525 | 0.21481 | 19 | 0.21765 | 0.21675 | 0.21571 | 0.21524 | 0.21398
Tumut | 848/1 | 66 | Adelong Tee | Batlow ZS | 21 | 8.782 | 8.7737 | 8.7941 | 8.8107 | 8.816 | 25 | 10.0726 | 10.0778 | 10.0781 | 10.0742 | 10.0805
Tumut | 848/2 | 66 | Batlow ZS | Tumbarumba ZS | 22 | 7.6509 | 7.6541 | 7.6739 | 7.6944 | 7.7003 | 26 | 8.5125 | 8.5157 | 8.5191 | 8.5098 | 8.5173
Tumut | 848/3 | 66 | TransGrid Tumut 132/66kV STS | Adelong Tee | 21 | 9.8721 | 9.8726 | 9.8866 | 9.9064 | 9.9018 | 25 | 11.1166 | 11.1211 | 11.1241 | 11.1199 | 11.1281
Tumut | 850:TAL | 66 | TransGrid Tumut 132/66kV STS | Talbingo ZS | 18 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 22 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 19.6576
Wagga (Copland St) | 83L | 66 | Hammond Ave ZS | Bomen ZS | 54 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Uranquinty ZS | 28 | 7.941 | 7.9678 | 8.0004 | 8.0333 | 8.0305 | 34 | 7.2926 | 7.356 | 7.4286 | 7.5027 | 7.568
Wagga (Copland St) | 840/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bulgary ZS | 15 | 3.4387 | 3.4413 | 3.4512 | 3.4607 | 3.4716 | 25 | 3.0987 | 3.1004 | 3.11 | 3.1144 | 3.1143
Wagga (Copland St) | 840/2 | 66 | Bulgary ZS | Lockhart ZS | 15 | 3.2818 | 3.2819 | 3.2946 | 3.3036 | 3.3147 | 24 | 2.973 | 2.975 | 2.9839 | 2.9889 | 2.9918
Wagga (Copland St) | 840/3 | 66 | Lockhart Tee | Kywong ZS | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M/1 | 66 | Uranquinty ZS | Henty ZS | 15 | 2.3755 | 2.3874 | 2.4045 | 2.4281 | 2.4303 | 25 | 2.2949 | 2.293 | 2.2924 | 2.2933 | 2.3029
Wagga (Copland St) | 83M/2 | 66 | Henty ZS | Culcairn ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8W9 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Ashmont ZS | 34 | 26.4489 | 26.321 | 26.2502 | 26.2149 | 26.1722 | 39 | 25.1212 | 25.2758 | 25.4665 | 25.6333 | 25.7992
Wagga (Copland St) | 8WF/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bourkelands Tee | 34 | 11.9495 | 12.0711 | 12.1194 | 12.1889 | 12.3042 | 39 | 11.0619 | 11.1867 | 11.2849 | 11.393 | 11.5294
Wagga (Copland St) | 8WF/2 | 66 | Bourkelands Tee | Kooringal ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WF/3 | 66 | Bourkelands Tee | Bourkelands ZS | 42 | 11.9495 | 12.0711 | 12.1194 | 12.1889 | 12.3042 | 46 | 11.0619 | 11.1867 | 11.2849 | 11.393 | 11.5294
Wagga (Copland St) | 8WM | 66 | Hammond Ave ZS | Morrow St ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WO | 66 | Ashmont ZS | Bourkelands ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WP | 66 | Morrow St ZS | Cartwrights Hill ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WR | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 7.4587 | 7.4478 | 7.4373 | 7.4825 | 7.4282 | 60 | 8.1679 | 8.306 | 8.4537 | 8.612 | 8.7671
Wagga (Copland St) | 8WT | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 7.0284 | 7.0182 | 7.0082 | 7.0508 | 6.9996 | 60 | 7.6967 | 7.8268 | 7.966 | 8.1152 | 8.2613
Wagga (Copland St) | 8WG | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Kooringal ZS | 34 | 17.5776 | 17.7856 | 18.1263 | 18.2914 | 18.6713 | 39 | 15.8122 | 15.9469 | 15.9644 | 16.0226 | 16.025
Wagga North | 99U | 132 | TransGrid Wagga North 132/66kV STS | Sebastopol Sw Stn | 128 | 106.066 | 106.066 | 106.066 | 106.066 | 106.066 | 143 | 108.6116 | 108.6116 | 108.6116 | 108.6116 | 108.6116
Wagga North | 9J6 | 132 | Sebastopol Sw Stn | Temora 132/66 STS | 128 | 29.1807 | 29.3035 | 29.4187 | 29.6452 | 29.8124 | 143 | 30.6032 | 31.167 | 31.7033 | 32.1611 | 32.7102
Wagga North | 9J5/1 | 132 | TransGrid Wagga North 132/66kV STS | Junee 132/66/11kV ZS | 140 | 37.139 | 37.2954 | 37.442 | 37.7303 | 37.9431 | 157 | 40.5671 | 41.3144 | 42.0253 | 42.6321 | 43.36
Wagga North | 9J5/2 | 132 | Junee 132/66/11kV ZS | Temora 132/66 STS | 140 | 27.5405 | 27.6674 | 27.8021 | 28.041 | 28.2204 | 157 | 27.264 | 27.8457 | 28.3993 | 28.8723 | 29.4288
Wagga North | 30-90 | 66 | Junee ZS | Coolamon ZS | 6 | 4.9697 | 4.9611 | 4.9766 | 4.9677 | 4.9668 | 9 | 4.6034 | 4.6466 | 4.6769 | 4.7199 | 4.7441
Wagga North | 834:JUN | 66 | Junee ZS | Bethungra ZS | 11 | 1.0544 | 1.0504 | 1.0458 | 1.0404 | 1.0366 | 19 | 1.023 | 1.0253 | 1.0268 | 1.0296 | 1.0293
Wagga North | 83C/1 | 66 | TransGrid Wagga North 132/66kV STS | Oura ZS | 24 | 3.7836 | 3.7684 | 3.768 | 3.7703 | 3.7554 | 28 | 3.3818 | 3.4036 | 3.4186 | 3.4297 | 3.4533
Wagga North | 83C/2 | 66 | Oura ZS | Forest Hill ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga North | 83G | 66 | TransGrid Wagga North 132/66kV STS | Bomen ZS | 34 | 17.7413 | 17.8644 | 20.0929 | 24.9311 | 29.745 | 39 | 16.9266 | 17.1804 | 19.5168 | 24.48 | 29.4528
Wagga North | 83J | 66 | Bomen ZS | Cartwrights Hill ZS | 34 | 8.8633 | 8.9992 | 9.1449 | 9.2977 | 9.4398 | 39 | 8.7561 | 9.0519 | 9.2971 | 9.5784 | 9.8734
Wagga North | 850:BET | 66 | Bethungra ZS | Cootamundra ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Wagga North | 7CH/1 | 33 | Cartwrights Hill ZS | Euberta ZS | 4 | 1.7582 | 1.7424 | 1.7342 | 1.7264 | 1.7149 | 6 | 1.383 | 1.3758 | 1.3757 | 1.3755 | 1.3711
Wagga North | 7CH/2 | 33 | Euberta ZS | Ganmurra ZS | 4 | 0.52998 | 0.51816 | 0.50965 | 0.49937 | 0.49238 | 6 | 0.50841 | 0.50566 | 0.50325 | 0.50378 | 0.50301
Wagga North | Oura-Mates Gully | 33 | Oura ZS | Mates Gully ZS | 3 | 1.6091 | 1.601 | 1.586 | 1.5831 | 1.5711 | 6 | 1.5049 | 1.5009 | 1.4958 | 1.4928 | 1.4929
Wagga North | Mates Gully-Tarcutta | 33 | Mates Gully ZS | Tarcutta ZS | 4 | 1.0405 | 1.0398 | 1.035 | 1.0362 | 1.0297 | 7 | 1.0173 | 1.0192 | 1.0203 | 1.0243 | 1.0281
Wagga North | 8WJ | 66 | TransGrid Wagga North 132/66kV STS | Forest Hill ZS | 11 | 5.1569 | 5.1423 | 5.1051 | 5.1061 | 5.1043 | 19 | 5.1333 | 5.116 | 5.0914 | 5.1261 | 5.0779
Yanco | 840/4 | 66 | Narrandra ZS | Kywong ZS | 16 | 0.43035 | 0.43728 | 0.44399 | 0.45065 | 0.45819 | 25 | 0.31128 | 0.31562 | 0.31873 | 0.3252 | 0.33204
Yanco | 841:YNC | 66 | TransGrid Yanco 132/33/66kV STS | Narrandera ZS | 15 | 10.2535 | 10.288 | 10.3541 | 10.4443 | 10.5149 | 25 | 8.5459 | 8.6354 | 8.7809 | 8.9108 | 9.0479
Yanco | 7L3 | 33 | TransGrid Yanco 132/33/66kV STS | Cudgel ZS | 8 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 13 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Yanco | 7L6/1 | 33 | TransGrid Yanco 132/33/66kV STS | Whitton / Murrami Tee | 15 | 6.6147 | 6.5722 | 6.5497 | 6.4904 | 6.4189 | 18 | 5.313 | 5.3135 | 5.3192 | 5.3185 | 5.3427
Yanco | 7L6/2 | 33 | Whitton / Murrami Tee | Whitton ZS | 8 | 3.978 | 3.9578 | 3.9689 | 3.9437 | 3.8957 | 13 | 2.6174 | 2.6078 | 2.6001 | 2.5847 | 2.6099
Yanco | 7L6/3 | 33 | Whitton / Murrami Tee | Murrami ZS | 6 | 1.434 | 1.4407 | 1.4383 | 1.4428 | 1.4495 | 9 | 1.3952 | 1.4186 | 1.4482 | 1.4782 | 1.5003
Yanco | 7L5/1 | 33 | TransGrid Yanco 132/33/66kV STS | Yanco ZS | 8 | 11.481 | 11.4986 | 11.4887 | 11.4671 | 11.4732 | 13 | 9.0547 | 9.0898 | 9.1451 | 9.1812 | 9.2307
Yanco | 7L5/2 | 33 | Yanco ZS | Leeton ZS | 6 | 8.9553 | 8.9625 | 8.9503 | 8.9198 | 8.9131 | 9 | 7.8889 | 7.8782 | 7.8824 | 7.8735 | 7.8706
Yanco | 7L4 | 33 | TransGrid Yanco 132/33/66kV STS | Leeton ZS | 31 | 9.7016 | 9.7094 | 9.6962 | 9.6631 | 9.6559 | 34 | 8.2176 | 8.2064 | 8.2108 | 8.2016 | 8.1986
Yass | 971(1) | 132 | TransGrid Yass 330/132/66kV STS | Cullerin Range Wind Farm | 106 | 75.9482 | 75.9786 | 76.1789 | 76.1454 | 76.1391 | 119 | 78.4982 | 78.7477 | 78.9624 | 78.8429 | 78.8119
Yass | 971(2) | 132 | Cullerin Range Wind Farm | Gunning Wind Farm | 140 | 48.3233 | 48.3265 | 48.4771 | 48.3386 | 48.3989 | 157 | 49.2138 | 49.4576 | 49.6314 | 49.4576 | 49.5342
Yass | 971(3) | 132 | Cullerin Range Wind Farm | Goulburn 132/66/33kV STS | 106 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0
Yass | 976/2 (M) | 132 | TransGrid 132kV Line 976/2(Y) / Murrumbateman Tee | Murrumbateman ZS | 42 | 6.118 | 6.1226 | 6.1982 | 6.1717 | 6.1692 | 82 | 7.5482 | 7.6626 | 7.816 | 7.9716 | 8.1076
Yass | 824 | 66 | TransGrid Yass 330/132/66kV STS | Yass ZS | 12 | 13.5161 | 13.5875 | 13.6621 | 13.8181 | 13.8362 | 18 | 16.3804 | 16.5261 | 16.6065 | 16.7579 | 16.8863
Yass | 823/5 | 66 | Yass ZS | Marilba ZS | 12 | 1.399 | 1.415 | 1.4216 | 1.4296 | 1.4392 | 18 | 1.6284 | 1.6447 | 1.6677 | 1.6944 | 1.7117

## BSP
Connection Point | Forecast PF | Summer Forecast (POE50 MVA) |  |  |  |  | Forecast PF | Winter Forecast (POE50 MVA) |  |  |  |  | Major Embedded Generation (MW)
|  | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 |  | 2025 | 2026 | 2027 | 2028 | 2029
Albury (Corowa) | 0.99112 | 14.6423 | 14.5641 | 14.5766 | 14.6332 | 14.6753 | 0.99554 | 13.0801 | 13.1427 | 13.1112 | 13.1186 | 13.1662 | 30
Albury (Mulwala) | 0.9895 | 13.0379 | 13.0655 | 13.0568 | 13.1002 | 13.124 | 0.99727 | 10.8027 | 10.9002 | 10.9976 | 11.1066 | 11.2006 | 5
Albury (Union Rd + Jelbart) | 0.99436 | 87.4964 | 88.386 | 89.0465 | 89.8653 | 90.4133 | 0.99516 | 81.6313 | 82.4212 | 83.5121 | 84.3899 | 85.4265 | 0
Armidale | 0.98587 | 29.878 | 30.0561 | 30.2212 | 30.4629 | 30.613 | 0.99813 | 43.0053 | 43.1516 | 43.1529 | 43.4277 | 43.615 | 10
Balranald | 0.99921 | 3.8371 | 3.8477 | 3.8568 | 3.867 | 3.8859 | 0.97294 | 2.7539 | 2.7595 | 2.7647 | 2.7815 | 2.7863 | 0
Beryl | 0.97443 | 78.3288 | 79.1492 | 78.6719 | 79.6445 | 79.841 | 0.97414 | 84.1158 | 84.4813 | 84.0378 | 84.1124 | 84.3967 | 87
Boambee South | 0.99298 | 17.1802 | 17.2932 | 17.3765 | 17.4357 | 17.532 | 0.99073 | 18.1339 | 18.3318 | 18.603 | 18.8063 | 19.0747 | 0
Broken Hill 22kV | 0.99043 | 38.8551 | 40.3487 | 40.3552 | 40.2415 | 40.234 | 0.9986 | 36.0861 | 38.3763 | 38.3835 | 38.47 | 38.4284 | 50
Casino | 0.97142 | 28.0588 | 28.2199 | 28.3777 | 28.5433 | 28.7427 | 0.99049 | 23.8741 | 24.0344 | 24.2368 | 24.3585 | 24.6117 | 0
Coffs Harbour | 0.99694 | 58.8512 | 58.8708 | 59.2098 | 59.1545 | 59.1968 | 0.99891 | 62.7224 | 63.5799 | 64.4339 | 65.3885 | 66.1138 | 0
Coleambally | 0.97089 | 12.2537 | 12.308 | 12.3918 | 12.4818 | 12.5591 | 0.9538 | 9.8563 | 9.9305 | 9.998 | 10.1084 | 10.1681 | 5
Cooma 132kV | 0.89849 | 35.7752 | 35.677 | 35.8014 | 35.6914 | 35.6569 | 0.93267 | 52.3449 | 52.3402 | 52.1897 | 52.4454 | 52.3131 | 118
Cooma 66kV | 0.99633 | 14.0762 | 14.0198 | 14.1331 | 14.1133 | 14.2069 | 0.9843 | 23.7494 | 23.7837 | 23.7768 | 23.9672 | 23.9749 | 1.1
Cowra | 0.99593 | 30.3894 | 30.8754 | 31.2582 | 32.1008 | 32.7902 | 0.99894 | 27.0889 | 27.3266 | 27.6515 | 27.9354 | 28.2246 | 22.5
Darlington Point | 0.89622 | 23.8057 | 24.0069 | 24.2204 | 24.4575 | 24.6477 | 0.92969 | 23.6037 | 24.2838 | 24.9974 | 25.7365 | 26.4915 | 85
Deniliquin | 0.98599 | 47.4761 | 47.7067 | 48.0317 | 48.3674 | 48.5435 | 0.99166 | 38.6086 | 38.8189 | 39.1811 | 39.5518 | 39.9057 | 0
Dorrigo | 0.98675 | 2.4308 | 2.4068 | 2.3931 | 2.4053 | 2.3864 | 0.99192 | 2.7201 | 2.718 | 2.7172 | 2.7204 | 2.7201 | 0
Dunoon | 0.9838 | 6.5625 | 6.6133 | 6.6954 | 6.7459 | 6.8282 | 0.99072 | 6.9827 | 7.0683 | 7.1611 | 7.2521 | 7.3085 | 0
Evans Lane | 0.99717 | 39.3387 | 39.2998 | 39.4793 | 39.7136 | 39.8085 | 0.99926 | 53.9952 | 54.197 | 54.4646 | 54.7327 | 54.6406 | 0
Finley 132kV | 0.99202 | 92.6615 | 92.0521 | 92.5912 | 94.0031 | 93.8557 | 0.98665 | 97.8041 | 97.6173 | 97.1622 | 97.774 | 98.6515 | 0
Finley 66kV | 0.99358 | 15.1752 | 15.0781 | 15.1725 | 15.1908 | 15.2282 | 0.99032 | 14.9335 | 15.4898 | 15.9831 | 16.4599 | 16.8622 | 2.5
Forbes | 0.99282 | 31.6821 | 31.6973 | 31.7489 | 31.7355 | 31.7664 | 0.99428 | 25.3001 | 25.36 | 25.3945 | 25.4525 | 25.4978 | 54.1
Glen Innes | 0.95369 | 11.2179 | 11.2511 | 11.3101 | 11.3477 | 11.384 | 0.98485 | 14.8072 | 15.0523 | 15.2709 | 15.5305 | 15.7252 | 5.5
Griffith | 0.9991 | 92.9883 | 92.7341 | 92.8057 | 92.72 | 92.9221 | 0.99977 | 63.3877 | 64.7119 | 66.0522 | 67.5141 | 68.7515 | 0
Gunnedah 66kV | 0.97578 | 23.3883 | 23.4053 | 23.3015 | 23.2644 | 23.2965 | 0.98028 | 25.7291 | 25.9841 | 26.3401 | 26.5935 | 26.8767 | 7
Hawks Nest | 0.996 | 8.6314 | 8.7013 | 8.7157 | 8.7599 | 8.8251 | 0.99664 | 8.5112 | 8.6121 | 8.7047 | 8.8613 | 8.9345 | 0
Herons Ck | 0.99183 | 12.1707 | 12.1704 | 12.2306 | 12.254 | 12.2873 | 0.99783 | 11.9489 | 12.1979 | 12.4998 | 12.7766 | 13.044 | 0
Inverell | 0.96705 | 34.9962 | 35.5654 | 36.2106 | 36.8107 | 37.6074 | 0.9781 | 39.6425 | 40.6743 | 41.4133 | 41.9178 | 42.4073 | 22.5
Kempsey 33kV | 0.99359 | 30.1807 | 30.7278 | 31.2075 | 31.6139 | 32.0365 | 0.9989 | 31.6279 | 32.0417 | 32.6214 | 33.1009 | 33.5954 | 0
Koolkhan | 0.99808 | 52.5297 | 52.6699 | 52.6831 | 52.6661 | 52.7253 | 0.99834 | 45.4848 | 45.5609 | 45.6731 | 45.6899 | 45.8644 | 0
Lismore 132kV | 0.99339 | 85.3151 | 85.5183 | 85.6879 | 86.159 | 86.4893 | 0.99143 | 66.3418 | 66.4255 | 66.5852 | 66.7652 | 66.7487 | 37.5
Macksville | 0.99792 | 9.0893 | 9.1904 | 9.2396 | 9.3251 | 9.4021 | 0.99864 | 9.6769 | 9.7392 | 9.7771 | 9.8305 | 9.8836 | 0
Manildra | 0.9495 | 10.2578 | 10.2935 | 10.3057 | 10.2741 | 10.3059 | 0.96436 | 9.9788 | 9.9875 | 9.9843 | 9.9853 | 9.9854 | 48.5
Marulan | 0.98817 | 52.5197 | 53.9883 | 55.5483 | 56.8731 | 58.2879 | 0.98891 | 63.9861 | 66.5105 | 69.1632 | 71.3877 | 73.904 | 118
Merbein | 0.93363 | 11.3456 | 11.2198 | 11.1378 | 11.1175 | 11.2713 | 0.98958 | 9.6745 | 9.8411 | 9.7827 | 9.7726 | 9.809 | 0
Mildura | 0.95531 | 22.0013 | 22.909 | 22.951 | 23.6394 | 24.4784 | 0.99612 | 17.2146 | 17.2407 | 17.3268 | 17.3315 | 17.2124 | 3.3
Molong | 0.9376 | 4.9519 | 5.0363 | 5.0768 | 5.1417 | 5.1522 | 0.90569 | 5.8815 | 6.0875 | 6.2382 | 6.4173 | 6.611 | 30
Moree | 0.99673 | 27.1582 | 27.5369 | 27.7687 | 28.1686 | 28.4736 | 0.99677 | 36.9532 | 36.9822 | 37.5026 | 37.8245 | 38.3077 | 66
Morven | 0.99599 | 7.4416 | 7.5614 | 7.6515 | 7.7818 | 7.8537 | 0.99645 | 7.7941 | 7.8493 | 7.9138 | 7.9444 | 8.0102 | 0
Mudgee | 0.98825 | 23.7529 | 23.9379 | 23.9522 | 23.9859 | 23.8923 | 0.99603 | 24.6661 | 25.0149 | 25.4655 | 25.8693 | 26.2604 | 0
Mullumbimby | 0.9962 | 54.3669 | 55.8059 | 57.3099 | 58.5916 | 60.241 | 0.99862 | 63.6433 | 64.425 | 65.1845 | 66.2818 | 67.0288 | 0
Munyang | 0.92051 | 3.7468 | 3.7739 | 3.7923 | 3.8023 | 3.8242 | 0.94774 | 30.0068 | 30.1256 | 30.3406 | 30.6394 | 30.6609 | 0
Murrumbateman | 0.99091 | 6.142 | 6.1533 | 6.2301 | 6.1998 | 6.2044 | 0.99947 | 7.55 | 7.6656 | 7.8185 | 7.9745 | 8.1105 | 0
Murrumburrah | 0.99384 | 35.3964 | 35.3961 | 35.3172 | 35.3765 | 35.4898 | 0.9976 | 39.6911 | 39.7796 | 39.7195 | 39.8168 | 39.9214 | 5
Nambucca | 0.98762 | 7.182 | 7.2218 | 7.3055 | 7.384 | 7.4393 | 0.99441 | 8.688 | 8.7436 | 8.8119 | 8.8575 | 8.9196 | 0
Narrabri | 0.9833 | 37.1706 | 37.2507 | 37.2136 | 37.2075 | 37.1767 | 0.98411 | 43.8357 | 43.9675 | 44.2308 | 44.3714 | 44.3705 | 16
Orange 132kV | 0.98259 | 171.4383 | 174.921 | 178.6695 | 182.1123 | 185.618 | 0.98853 | 177.4609 | 182.088 | 186.673 | 191.445 | 195.472 | 145
Orange 66kV | 0.99314 | 50.698 | 50.756 | 50.7217 | 50.7612 | 50.7386 | 0.99239 | 65.4572 | 65.8644 | 66.0589 | 66.486 | 66.9126 | 0
Panorama | 0.99567 | 69.5662 | 69.4424 | 69.6359 | 69.4218 | 69.437 | 0.98979 | 77.429 | 78.2539 | 79.132 | 79.8272 | 80.5805 | 10
Parkes 132kV | 0.98006 | 33.9606 | 39.3382 | 48.0077 | 57.0591 | 60.2741 | 0.97994 | 34.9745 | 43.6284 | 52.3272 | 61.3971 | 64.703 | 0
Parkes 66kV | 0.96617 | 27.9528 | 27.9111 | 27.9196 | 27.9451 | 27.9898 | 0.98721 | 30.9505 | 31.5588 | 32.2759 | 32.8496 | 33.6276 | 94
Port Macquarie | 0.99408 | 70.0588 | 70.1608 | 70.4127 | 70.9935 | 71.3547 | 0.9953 | 80.9492 | 81.583 | 82.6749 | 83.7027 | 84.5186 | 0
Queanbeyan 132kV | 0.93715 | 9.1684 | 9.4469 | 9.7214 | 10.1601 | 10.4215 | 0.97804 | 11.4811 | 12.0184 | 12.5892 | 13.2466 | 13.9176 | 0
Queanbeyan 66kV | 0.99635 | 54.517 | 60.1131 | 65.7649 | 71.2636 | 77.1266 | 0.99725 | 71.4176 | 77.9321 | 84.3915 | 90.5816 | 96.8881 | 0
Raleigh | 0.98641 | 9.4002 | 9.3906 | 9.3799 | 9.3926 | 9.383 | 0.99851 | 11.3077 | 11.4983 | 11.6627 | 11.835 | 12.0268 | 0
Robinvale | 0.97761 | 6.2661 | 6.3155 | 6.3975 | 6.442 | 6.4971 | 0.97534 | 3.0831 | 3.1066 | 3.0855 | 3.0923 | 3.0788 | 0
Snowy Adit | 0.96475 | 4.1119 | 4.1167 | 4.0769 | 4.0628 | 4.0453 | 0.99106 | 7.8437 | 8.121 | 8.3176 | 8.5401 | 8.784 | 0
Stroud | 0.98182 | 37.9444 | 38.1559 | 38.3172 | 38.5624 | 38.6443 | 0.9963 | 40.754 | 41.2875 | 41.7462 | 42.2186 | 42.7087 | 0
Tamworth | 0.99288 | 111.9572 | 111.8808 | 119.6327 | 121.9533 | 123.1166 | 0.99685 | 104.8388 | 113.1879 | 116.353 | 119.222 | 122.334 | 0
Taree 33kV | 0.98405 | 31.2247 | 31.2299 | 31.2676 | 31.3365 | 31.381 | 0.98478 | 26.9623 | 27.1885 | 27.5042 | 27.7541 | 27.9612 | 0
Taree 66kV | 0.99712 | 48.9896 | 49.3949 | 49.533 | 49.8263 | 50.3621 | 0.99857 | 57.5778 | 58.1189 | 58.7656 | 59.1454 | 59.771 | 0
Tenterfield | 0.97775 | 4.286 | 4.3311 | 4.3447 | 4.3684 | 4.4042 | 0.99394 | 5.729 | 5.7859 | 5.8159 | 5.8833 | 5.9521 | 0
Terranora | 0.99546 | 116.4888 | 118.6854 | 119.5446 | 121.4382 | 123.1386 | 0.99959 | 93.8979 | 94.6979 | 95.7297 | 96.7805 | 97.6977 | 30
Tumut | 0.94718 | 30.8224 | 30.8611 | 30.8757 | 30.8563 | 31.0986 | 0.97653 | 32.1487 | 32.1936 | 32.2381 | 32.2836 | 32.3791 | 14
Upper Tumut | 0.99564 | 1.1092 | 1.1106 | 1.1096 | 1.1118 | 1.1131 | 0.99894 | 2.0229 | 2.0212 | 2.0156 | 2.0213 | 2.0181 | 0
Wagga 66kV | 0.99165 | 76.7836 | 76.7742 | 77.1316 | 76.6521 | 76.5375 | 0.99852 | 77.8266 | 77.8488 | 78.2457 | 78.1542 | 78.2637 | 0
Wagga North 132kV | 0.97354 | 66.6517 | 66.9325 | 67.1983 | 67.7258 | 68.1615 | 0.99096 | 71.1912 | 72.5326 | 73.7297 | 74.8291 | 76.1194 | 263
Wagga North 66kV | 0.98705 | 21.6433 | 21.8785 | 24.2886 | 26.3161 | 28.6429 | 0.99273 | 24.0451 | 24.2792 | 26.7408 | 29.249 | 31.7401 | 0
Waggamba | 0.99239 | 19.3906 | 19.3509 | 19.3608 | 19.4188 | 19.4751 | 0.9982 | 23.8854 | 23.9706 | 23.9586 | 23.9612 | 24.0181 | 0
Wallerawang 132kV | 0.86102 | 36.1404 | 37.0509 | 37.8467 | 38.5641 | 39.4037 | 0.87103 | 37.1271 | 37.9354 | 38.61 | 39.499 | 40.2546 | 0
Wallerawang 66kV | 0.99756 | 5.3357 | 5.4072 | 5.4943 | 5.5733 | 5.6525 | 0.98758 | 6.2826 | 6.3301 | 6.3581 | 6.412 | 6.4644 | 0
Wellington 132kV | 0.99725 | 168.4932 | 169.3566 | 170.8175 | 193.9648 | 217.2605 | 0.99813 | 161.5758 | 162.1258 | 184.8669 | 208.2492 | 208.9056 | 261.3
Yanco | 0.96428 | 41.6008 | 41.7659 | 41.8893 | 42.022 | 42.0509 | 0.98308 | 34.6841 | 34.748 | 34.7889 | 34.779 | 34.7893 | 16.5
Yass 132kV | 0.88586 | 49.5389 | 50.1537 | 50.6094 | 50.7813 | 51.7551 | 0.98901 | 39.3933 | 40.4757 | 41.0976 | 42.1506 | 42.7809 | 76.5
Yass 66kV | 0.97839 | 13.931 | 14.1351 | 14.2618 | 14.3488 | 14.6518 | 0.98844 | 16.819 | 17.2212 | 17.6951 | 18.0811 | 18.4119 | 0

## ZS Export
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (POE50 MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 24/25 | 25/26 | 26/27 | 27/28 | 28/29
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 33 | -0.99862 | 9.573 | 10.094 | 10.591 | 11.065 | 11.519 | 16.76 | 44
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 33 | -0.68861 | 8.715 | 9.195 | 9.652 | 10.087 | 10.505 | 16.12 | 50
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 16.5 | -0.9989 | 9.114 | 9.621 | 10.102 | 10.561 | 11.001 | 17.1 | 43
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | -0.9196 | 10.69 | 11.268 | 11.819 | 12.344 | 12.849 | 23.91 | 35
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 220 | 0.72548 | 0 | 0 | 0 | 0 | 0 | 0 | 647
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 33 | -0.99385 | 6.205 | 6.614 | 6.999 | 7.364 | 7.712 | 10.61 | 26
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 27.5 | 0.99759 | 2.831 | 2.994 | 3.149 | 3.296 | 3.437 | 5.48 | 22
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 33 | -0.99958 | 8.846 | 9.327 | 9.784 | 10.221 | 10.639 | 16.79 | 28
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 22 | -0.98812 | 8.045 | 8.502 | 8.936 | 9.349 | 9.745 | 15.86 | 34
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 33 | -0.73636 | 16.632 | 17.641 | 18.596 | 19.504 | 20.372 | 30.43 | 41
Lismore | Ballina 132kV | 132/66 | 75/112 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lismore | Dunoon | 132/11 | 10 | 10 |  | 11 | -0.94009 | 3.466 | 3.664 | 3.852 | 4.031 | 4.202 | 8.05 | 24
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.82238 | 8.068 | 8.512 | 8.933 | 9.336 | 9.721 | 19.45 | 16
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 11 | 0.33441 | 3.356 | 3.525 | 3.687 | 3.842 | 3.991 | 7.4 | 27
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 17.6 | -0.95325 | 4.185 | 4.402 | 4.608 | 4.806 | 4.996 | 8.18 | 17
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 264 | 0.87415 | 31.262 | 33.173 | 34.977 | 36.69 | 38.324 | 0 | 24
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 25.3 | -0.98893 | 8.559 | 9.073 | 9.559 | 10.021 | 10.463 | 16.38 | 29
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 52.8 | -0.87756 | 3.264 | 3.449 | 3.624 | 3.791 | 3.951 | 7.42 | 17
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 33 | 0.95044 | 8.207 | 8.7 | 9.167 | 9.611 | 10.035 | 16.68 | 35
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 11 | -0.98966 | 5.198 | 5.508 | 5.801 | 6.081 | 6.348 | 11.56 | 25
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | -0.99228 | 6.239 | 6.607 | 6.955 | 7.287 | 7.604 | 13.66 | 26
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 11 | -0.79262 | 4.058 | 4.29 | 4.51 | 4.72 | 4.921 | 8.85 | 25
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 2.75 | 0 | 0.363 | 0.378 | 0.393 | 0.408 | 0.422 | 0.94 | 16
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 33 | -0.63281 | 9.32 | 9.832 | 10.319 | 10.784 | 11.229 | 18.79 | 33
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 3.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.96048 | 0.413 | 0.434 | 0.453 | 0.472 | 0.49 | 0.97 | 26
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 5.5 | -0.77781 | 0.337 | 0.355 | 0.371 | 0.387 | 0.402 | 0.7 | 25
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.80731 | 0.334 | 0.352 | 0.369 | 0.386 | 0.402 | 0.76 | 19
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 27.5 | -0.58612 | 6.673 | 7.061 | 7.429 | 7.78 | 8.115 | 12.6 | 28
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 26.95 | -0.86319 | 6.476 | 6.799 | 7.107 | 7.403 | 7.687 | 13.79 | 16
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | -0.50882 | 1.664 | 1.771 | 1.871 | 1.967 | 2.058 | 2.82 | 23
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.076696 | 6.336 | 6.687 | 7.02 | 7.337 | 7.642 | 11.73 | 42
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.66 | 0.95 | 0.15 | 0.156 | 0.162 | 0.168 | 0.174 | 0.35 | 10
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.55 | 0.79444 | 0.139 | 0.146 | 0.154 | 0.161 | 0.168 | 0.26 | 13
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | -0.96425 | 0.555 | 0.581 | 0.606 | 0.63 | 0.653 | 1.18 | 14
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 25.3 | -0.925 | 6.876 | 7.32 | 7.739 | 8.136 | 8.514 | 12.47 | 39
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 33 | 1 | 5.161 | 5.488 | 5.797 | 6.09 | 6.37 | 9.84 | 24
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 50.6 | 0.97718 | 10.107 | 10.809 | 11.469 | 12.092 | 12.685 | 18.1 | 27
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 33 | 0.92349 | 6.365 | 6.824 | 7.254 | 7.66 | 8.045 | 12.72 | 47
Coffs Harbour | Dorrigo | 66/11, 132/11 | 7.5/10 | 10 |  | 11 | 0.45429 | 1.923 | 2.024 | 2.119 | 2.211 | 2.299 | 2.82 | 26
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 17.6 | -0.99879 | 4.781 | 5.1 | 5.399 | 5.683 | 5.954 | 8.46 | 40
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 6.875 | 0.95 | 1.585 | 1.666 | 1.743 | 1.817 | 1.888 | 3.22 | 17
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 26.95 | -0.38075 | 4.991 | 5.371 | 5.726 | 6.061 | 6.378 | 8.51 | 36
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.24333 | 0.314 | 0.342 | 0.367 | 0.391 | 0.413 | 0.5 | 10
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 33 | -0.97918 | 8.407 | 8.989 | 9.535 | 10.052 | 10.543 | 14.97 | 38
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 33 | -0.99827 | 5.938 | 6.347 | 6.731 | 7.095 | 7.441 | 10.88 | 28
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 25.3 | -0.78994 | 4.485 | 4.788 | 5.072 | 5.341 | 5.598 | 8.88 | 29
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 33 | -0.88775 | 5.503 | 5.845 | 6.167 | 6.473 | 6.766 | 11.87 | 14
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.4 | -0.99975 | 0.928 | 0.987 | 1.044 | 1.097 | 1.149 | 1.72 | 37
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.3 | -0.78534 | 0.661 | 0.696 | 0.73 | 0.762 | 0.793 | 1.53 | 33
Kempsey | North St | 33/11 | 10 | 16 |  | 11 | 0.90209 | 3.788 | 4.002 | 4.204 | 4.398 | 4.583 | 8.02 | 40
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 16.5 | -0.63802 | 3.734 | 3.997 | 4.243 | 4.475 | 4.696 | 7.06 | 14
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 5.5 | 0.81717 | 1.348 | 1.439 | 1.525 | 1.606 | 1.683 | 2.76 | 34
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 13.75 | -0.78457 | 4.582 | 4.964 | 5.319 | 5.651 | 5.965 | 7.66 | 58
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 33 | 1 | 7.47 | 7.926 | 8.357 | 8.766 | 9.158 | 13.88 | 10
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.24993 | 0.581 | 0.606 | 0.631 | 0.655 | 0.677 | 1.33 | 14
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 33 | -0.99371 | 16.018 | 17.314 | 18.52 | 19.651 | 20.722 | 26.78 | 56
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 3.85 | 0.99745 | 1.44 | 1.536 | 1.626 | 1.711 | 1.792 | 2.91 | 33
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 8.8 | 0.98792 | 5.321 | 5.694 | 6.045 | 6.376 | 6.69 | 9.13 | 28
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 22 | 0.97532 | 4.07 | 4.351 | 4.614 | 4.863 | 5.1 | 7.41 | 56
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 16.5 | 0 | 6.476 | 6.894 | 7.288 | 7.662 | 8.019 | 12.6 | 32
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.4 | -0.69459 | 0.891 | 0.948 | 1.001 | 1.052 | 1.101 | 2.08 | 18
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | -0.78891 | 0.327 | 0.34 | 0.352 | 0.364 | 0.376 | 1.01 | 13
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.4 | 0.31804 | 2.022 | 2.143 | 2.258 | 2.367 | 2.471 | 4.9 | 16
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 22 | -0.99563 | 4.669 | 4.95 | 5.215 | 5.468 | 5.709 | 8.61 | 21
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 7.7 | -0.99912 | 4.269 | 4.591 | 4.893 | 5.176 | 5.445 | 7.63 | 51
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 5.5 | 0.86393 | 0.809 | 0.855 | 0.899 | 0.941 | 0.981 | 1.78 | 9
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.15 | -0.89703 | 1.283 | 1.347 | 1.408 | 1.467 | 1.524 | 2.8 | 27
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.95912 | 7.223 | 7.771 | 8.283 | 8.765 | 9.221 | 13.91 | 26
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 17.6 | -0.78977 | 5.542 | 5.965 | 6.361 | 6.734 | 7.087 | 9.98 | 38
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 6.875 | -0.99533 | 2.969 | 3.17 | 3.359 | 3.538 | 3.709 | 4.83 | 58
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 27.5 | -0.24254 | 4.575 | 4.853 | 5.116 | 5.366 | 5.605 | 8.6 | 19
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 17.6 | 0.99996 | 2.91 | 3.111 | 3.3 | 3.479 | 3.649 | 4.89 | 39
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 22 | 0.97823 | 5.623 | 5.986 | 6.329 | 6.654 | 6.964 | 10.33 | 13
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 11 | 0.44649 | 4.051 | 4.331 | 4.593 | 4.842 | 5.078 | 8.01 | 24
Stroud | Booral | 33/11 | 3 | 2.5 |  | 2.75 | 0.95 | 0.53 | 0.556 | 0.581 | 0.605 | 0.628 | 1.24 | 11
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.27196 | 1.348 | 1.415 | 1.479 | 1.54 | 1.6 | 2.82 | 10
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.89351 | 2.952 | 3.133 | 3.303 | 3.465 | 3.62 | 5.94 | 24
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.72852 | 3.495 | 3.734 | 3.958 | 4.17 | 4.372 | 6.76 | 21
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.15 | -0.21801 | 0.864 | 0.912 | 0.957 | 1 | 1.041 | 1.69 | 22
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 8.8 | -0.85166 | 1.376 | 1.447 | 1.515 | 1.579 | 1.642 | 2.81 | 32
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.034812 | 1.866 | 1.985 | 2.098 | 2.205 | 2.308 | 3.95 | 19
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 66 | 0.95757 | 0.199 | 0.199 | 0.199 | 0.199 | 0.199 | 0.01 | 1360
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 5.5 | 0.98724 | 1.058 | 1.113 | 1.166 | 1.216 | 1.264 | 2.08 | 17
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.918 | 4.392 | 4.651 | 4.896 | 5.13 | 5.354 | 7.63 | 16
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply | [5 empty] | -0.99118 | 3.681 | 3.87 | 4.049 | 4.22 | 4.384 | 2.74 | 22
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 2.75 | 0.94897 | 1.003 | 1.054 | 1.103 | 1.149 | 1.194 | 1.9 | 28
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 13.75 | -0.91397 | 9.839 | 10.15 | 10.443 | 10.722 | 10.987 | 9.46 | 21
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.22949 | 0.115 | 0.122 | 0.129 | 0.135 | 0.141 | 0.22 | 10
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 13.75 | -0.91191 | 5.481 | 5.873 | 6.239 | 6.586 | 6.915 | 6.32 | 22
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.9892 | 3.137 | 3.329 | 3.51 | 3.683 | 3.847 | 6.1 | 20
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 3.85 | 0.95 | 0.108 | 0.113 | 0.118 | 0.122 | 0.127 | 0.23 | 9
Armidale | Uralla | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 1.82 | 1.935 | 2.044 | 2.148 | 2.247 | 3.57 | 11
Armidale | Walcha South 66/22kV | 66/22 | 8 | 8/10 |  | 8.8 | 0.86374 | 0.465 | 0.475 | 0.485 | 0.495 | 0.505 | 1.06 | 18
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.3 | 0.26479 | 0.602 | 0.635 | 0.667 | 0.698 | 0.727 | 1.24 | 24
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.95 | 0.577 | 0.606 | 0.633 | 0.659 | 0.684 | 1.29 | 27
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | -0.51362 | 0.081 | 0.085 | 0.088 | 0.091 | 0.094 | 0.13 | 6
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 22 | -0.19612 | 3.561 | 3.751 | 3.931 | 4.104 | 4.269 | 6.95 | 24
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 5.5 | 0.48793 | 1.839 | 1.936 | 2.028 | 2.116 | 2.201 | 3.36 | 25
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.95 | 0.379 | 0.395 | 0.409 | 0.424 | 0.437 | 0.84 | 22
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.3 | -0.63372 | 1.037 | 1.089 | 1.14 | 1.188 | 1.234 | 2.2 | 27
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 33 | -0.67607 | 7.718 | 8.082 | 8.431 | 8.766 | 9.088 | 16 | 22
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | -0.11684 | 0.369 | 0.387 | 0.405 | 0.422 | 0.439 | 0.77 | 29
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.65 | 0.95 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0 | 75
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 5.5 | 0.95 | 0.524 | 0.542 | 0.558 | 0.574 | 0.59 | 1.51 | 21
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 5.5 | 0 | 0.212 | 0.216 | 0.219 | 0.222 | 0.225 | 0.61 | 2
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | -0.17256 | 0.047 | 0.049 | 0.05 | 0.051 | 0.053 | 0.13 | 9
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.4 | -0.13298 | 1.32 | 1.377 | 1.432 | 1.485 | 1.536 | 2.39 | 17
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.95 | 0.325 | 0.334 | 0.343 | 0.351 | 0.36 | 0.94 | 16
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 16.5 | -0.97325 | 11.696 | 11.833 | 11.965 | 12.093 | 12.216 | 7.04 | 14
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.944 | 0.678 | 0.691 | 0.705 | 0.718 | 0.731 | 2.92 | 13
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.98157 | 0.228 | 0.231 | 0.234 | 0.237 | 0.239 | 0.55 | 10
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 2.75 | 0.74366 | 0.161 | 0.163 | 0.165 | 0.167 | 0.169 | 0.56 | 14
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 33 | -0.17888 | 6.448 | 6.712 | 6.966 | 7.212 | 7.449 | 14.26 | 27
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.95 | 0.495 | 0.515 | 0.534 | 0.552 | 0.57 | 1.29 | 14
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.95 | 3.3 | 3.302 | 3.303 | 3.304 | 3.305 | 0.23 | 2
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | -0.95029 | 5.012 | 5.013 | 5.013 | 5.013 | 5.013 | 0.09 | 1760
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.39307 | 0.408 | 0.431 | 0.453 | 0.474 | 0.494 | 1.28 | 3
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 5.5 | 1 | 0.31 | 0.318 | 0.325 | 0.333 | 0.34 | 0.76 | 4
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 5.5 | -0.83205 | 1.234 | 1.337 | 1.432 | 1.521 | 1.605 | 2.57 | 42
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0 | 0.275 | 0.292 | 0.309 | 0.324 | 0.339 | 0.7 | 10
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.76822 | 4.499 | 4.674 | 4.842 | 5.004 | 5.162 | 10.71 | 20
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 11 | 0.011235 | 1.35 | 1.433 | 1.512 | 1.586 | 1.658 | 3.26 | 19
Narrabri | Wee Waa | 66/22 | 10 | 16 |  | 11 | 0.93248 | 1.25 | 1.304 | 1.356 | 1.406 | 1.455 | 3.15 | 28
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.15 | 0.70711 | 0.762 | 0.792 | 0.82 | 0.848 | 0.875 | 1.83 | 10
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.91141 | 7.798 | 8.389 | 8.941 | 9.461 | 9.954 | 13.31 | 28
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0 | 0.023 | 0.023 | 0.023 | 0.023 | 0.023 | 0.03
Tamworth | Attunga | 66/11 | 5 | 8 |  | 5.5 | 0.95 | 0.877 | 0.916 | 0.953 | 0.989 | 1.023 | 1.77 | 2
Tamworth | Barraba | 66/11 | 5 | 5 |  | 5.5 | 0.99752 | 0.921 | 0.971 | 1.018 | 1.063 | 1.106 | 2.12 | 24
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.1 | 0.91261 | 0.291 | 0.306 | 0.319 | 0.332 | 0.345 | 0.64 | 23
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.2 | 0.87287 | 0.047 | 0.048 | 0.05 | 0.052 | 0.053 | 0.15 | 3
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.65 | 0.67146 | 0.141 | 0.146 | 0.152 | 0.157 | 0.162 | 0.42 | 20
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.95 | 0.281 | 0.289 | 0.297 | 0.304 | 0.311 | 0.6 | 27
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 33 | 0.92452 | 3.105 | 3.315 | 3.513 | 3.7 | 3.878 | 4.26 | 13
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 17.6 | -0.24254 | 2.372 | 2.511 | 2.642 | 2.766 | 2.886 | 4.75 | 16
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.9 | 1.414 | 1.494 | 1.571 | 1.644 | 1.714 | 3.21 | 23
Tamworth | Murrurundi | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.68189 | 1.01 | 1.07 | 1.126 | 1.18 | 1.231 | 2.04 | 15
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 2.75 | 0.59927 | 0.524 | 0.542 | 0.56 | 0.577 | 0.593 | 1.28 | 20
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 33 | 0 | 7.283 | 7.79 | 8.267 | 8.718 | 9.147 | 13.56 | 8
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.95719 | 1.807 | 1.902 | 1.991 | 2.077 | 2.159 | 4.71 | 12
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.97881 | 0.065 | 0.067 | 0.069 | 0.07 | 0.072 | 0.19 | 9
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 50.6 | 0.99234 | 6.977 | 7.427 | 7.852 | 8.255 | 8.64 | 14.27 | 7
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 33 | 0.98478 | 8.103 | 8.636 | 9.139 | 9.615 | 10.069 | 14.99 | 19
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.86847 | 0.045 | 0.047 | 0.049 | 0.051 | 0.052 | 0.12 | 13
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 6.875 | 0.95 | 5.497 | 5.796 | 6.08 | 6.351 | 6.611 | 1.45 | 5
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 14.3 | -0.29914 | 2.531 | 2.638 | 2.742 | 2.841 | 2.937 | 6.88 | 15
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 11 | -0.52918 | 2.112 | 2.204 | 2.293 | 2.378 | 2.46 | 4.26 | 26
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | -0.91037 | 1.121 | 1.195 | 1.264 | 1.33 | 1.393 | 2.38 | 5
Beryl | Mudgee | 66/22, 132/22 | 18/30 | 30 |  | 33 | 0.28121 | 8.668 | 9.208 | 9.718 | 10.202 | 10.665 | 18.48 | 18
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 2.75 | 0 | 0.874 | 0.913 | 0.951 | 0.987 | 1.022 | 1.67 | 13
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 2.75 | 0.95 | 0.358 | 0.388 | 0.415 | 0.441 | 0.465 | 0.89 | 15
Wellington | Wellington 11kV | 132/11, 66/11 | 10 | 15 |  | 11 | 0.87432 | 2.553 | 2.741 | 2.917 | 3.083 | 3.241 | 5.49 | 7
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 11 | -0.44693 | 1.741 | 1.829 | 1.913 | 1.994 | 2.071 | 3.61 | 12
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 99 | 0 | 4.956 | 5.259 | 5.545 | 5.816 | 6.075 | 0
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 33 | 0.93834 | 3.083 | 3.263 | 3.434 | 3.597 | 3.753 | 7.27 | 7
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 33 | -0.97929 | 22.714 | 23.33 | 23.91 | 24.458 | 24.981 | 15.49 | 1250
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 25.3 | -0.97908 | 6.509 | 6.897 | 7.265 | 7.615 | 7.949 | 12.29 | 36
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 33 | -0.62403 | 13.456 | 14.026 | 14.565 | 15.078 | 15.568 | 17.92 | 17
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | -0.29562 | 0.598 | 0.639 | 0.677 | 0.714 | 0.748 | 1.21 | 28
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 13.2 | -0.82195 | 2.193 | 2.302 | 2.407 | 2.507 | 2.603 | 4.82 | 15
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.95 | 0.435 | 0.455 | 0.475 | 0.494 | 0.512 | 1.01 | 36
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 26.4 | -0.99725 | 12.995 | 13.177 | 13.352 | 13.519 | 13.681 | 8.35 | 565
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 11 | -0.063109 | 1.51 | 1.579 | 1.645 | 1.708 | 1.77 | 3.64 | 19
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 27.5 | 0.89755 | 1.047 | 1.1 | 1.15 | 1.198 | 1.244 | 2.15 | 7
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.37139 | 0.908 | 0.939 | 0.969 | 0.998 | 1.026 | 2.54 | 2
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.39248 | 0.258 | 0.261 | 0.265 | 0.268 | 0.272 | 0.79 | 48
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.1 | 0 | 0.02 | 0.021 | 0.022 | 0.023 | 0.024 | 0.04 | 23
Nyngan | Cobar CSA | 132/11 | 15/18 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Town | 66/22 | 8/11 | 10/13 |  | 12.1 | 0.95 | 2.481 | 2.627 | 2.765 | 2.896 | 3.022 | 5.25 | 20
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 33 | 0 | 5.349 | 5.676 | 5.985 | 6.278 | 6.558 | 0
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 11 | -0.20362 | 7.104 | 7.193 | 7.279 | 7.362 | 7.442 | 2.91 | 13
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply | [5 empty] | -0.95792 | 116.807 | 118.775 | 120.629 | 122.384 | 124.057 | 25.4 | 1
Broken Hill | Wilcannia 33kV | [5 empty] | -0.077023 | 0.12 | 0.121 | 0.121 | 0.122 | 0.123 | 0.36 | 8
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 5.5 | -0.97624 | 0.492 | 0.523 | 0.551 | 0.578 | 0.604 | 1.06 | 4
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.65 | 0.17044 | 0.27 | 0.273 | 0.277 | 0.28 | 0.283 | 0.93 | 7
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.65 | 0.70711 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.21 | 16
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | -0.81373 | 0.298 | 0.334 | 0.366 | 0.395 | 0.423 | 0.37 | 14
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.4 | 0.006252 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.24 | 30
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 3.85 | -0.53845 | 0.246 | 0.268 | 0.289 | 0.308 | 0.327 | 0.67 | 12
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 11 | -0.99854 | 7.188 | 7.647 | 8.081 | 8.492 | 8.885 | 12.01 | 58
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 33 | 0.94 | 4.878 | 5.24 | 5.579 | 5.898 | 6.201 | 8.27 | 33
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 33 | 0.55632 | 7.982 | 8.613 | 9.201 | 9.753 | 10.276 | 13.83 | 25
Orange | Orange West | 66/11 | 30 | 30 |  | 33 | -0.9965 | 7.069 | 7.564 | 8.03 | 8.469 | 8.887 | 12.21 | 19
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 2.75 | 0 | 0.57 | 0.592 | 0.613 | 0.633 | 0.653 | 1.57 | 23
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 26.4 | -0.75319 | 0.95 | 0.983 | 1.015 | 1.046 | 1.076 | 2.12 | 28
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.4 | 0.97115 | 1.362 | 1.452 | 1.538 | 1.619 | 1.696 | 2.89 | 12
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 22 | 0.90599 | 3.176 | 3.42 | 3.647 | 3.862 | 4.065 | 5.62 | 25
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 2.75 | -0.97958 | 0.91 | 0.957 | 1.001 | 1.044 | 1.086 | 1.94 | 24
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 33 | 0.80166 | 7.186 | 7.703 | 8.188 | 8.646 | 9.08 | 13.13 | 30
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 66 | 0 | 5.613 | 6.052 | 6.462 | 6.847 | 7.212 | 11.93 | 18
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 22 | -0.98915 | 8.576 | 9.192 | 9.769 | 10.314 | 10.832 | 15.17 | 30
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 16.5 | 0.87261 | 1.968 | 2.087 | 2.199 | 2.306 | 2.408 | 4.23 | 39
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 33 | -0.98567 | 6.315 | 6.66 | 6.988 | 7.302 | 7.602 | 12.99 | 7
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 11 | -0.99571 | 5.821 | 5.872 | 5.92 | 5.965 | 6.009 | 1.68 | 1547
Parkes | Trundle | 66/22 | 8 | 5 |  | 5.5 | 0.99 | 6.172 | 6.218 | 6.263 | 6.306 | 6.348 | 2.36 | 1712
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 11 | 0.75657 | 2.146 | 2.218 | 2.287 | 2.355 | 2.42 | 5.31 | 21
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 33 | 0.44721 | 3.997 | 4.227 | 4.446 | 4.655 | 4.854 | 9.14 | 33
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 7.7 | 0.62405 | 1.326 | 1.368 | 1.408 | 1.448 | 1.486 | 3.19 | 17
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 5.5 | 0.95 | 0.568 | 0.595 | 0.621 | 0.646 | 0.669 | 1.34 | 18
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.4 | 0.8732 | 0.294 | 0.313 | 0.331 | 0.347 | 0.363 | 0.45 | 8
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.76822 | 7.747 | 8.296 | 8.811 | 9.298 | 9.76 | 14.07 | 24
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.3 | -0.91531 | 0.7 | 0.743 | 0.783 | 0.821 | 0.858 | 1.35 | 10
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.70711 | 3.209 | 3.429 | 3.636 | 3.832 | 4.018 | 6.43 | 12
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 13.75 | -0.99966 | 4.766 | 5.138 | 5.485 | 5.81 | 6.119 | 8.25 | 20
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 13.75 | -0.58321 | 3.161 | 3.389 | 3.603 | 3.805 | 3.996 | 6 | 15
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | -0.9844 | 1.653 | 1.78 | 1.899 | 2.011 | 2.117 | 2.8 | 20
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 5.5 | -0.83222 | 0.428 | 0.452 | 0.475 | 0.497 | 0.519 | 0.72 | 47
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 22 | 0.92199 | 3.662 | 3.849 | 4.026 | 4.197 | 4.36 | 7.22 | 44
Cooma | Eucumbene | 66/11 | 0.6 |  |  | 0 | 0 | 0.038 | 0.039 | 0.041 | 0.042 | 0.043 | 0.08
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 33 | 0 | 3.087 | 3.249 | 3.401 | 3.544 | 3.679 | 3.98 | 41
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0 | 0.177 | 0.194 | 0.21 | 0.224 | 0.238 | 0.26 | 5
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 11 | -0.99135 | 1.674 | 1.802 | 1.922 | 2.034 | 2.141 | 2.84 | 23
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.65158 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0 | 1
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 0.99136 | 0.14 | 0.154 | 0.167 | 0.179 | 0.191 | 0.2 | 9
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 0 | 0.023 | 0.023 | 0.023 | 0.023 | 0.023 | 0 | 20
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 11 | 0.95 | 0.106 | 0.117 | 0.126 | 0.136 | 0.144 | 0.12 | 7
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0.8576 | 0 | 0 | 0 | 0 | 0 | 0 | 982
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.98276 | 0.034 | 0.034 | 0.034 | 0.034 | 0.034 | 0.03 | 5
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Bermagui | 33/11 | 5 | 5 |  | 5.5 | -0.96228 | 1.652 | 1.777 | 1.894 | 2.004 | 2.108 | 3.14 | 15
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0 | 0.29 | 0.314 | 0.337 | 0.358 | 0.378 | 0.57 | 17
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 2.75 | -0.98948 | 0.982 | 1.04 | 1.095 | 1.147 | 1.198 | 1.97 | 65
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.89359 | 1.528 | 1.621 | 1.708 | 1.791 | 1.871 | 3.47 | 11
Bega | Edrom | 66/11 | 5 | 5 |  | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.89443 | 5.035 | 5.344 | 5.636 | 5.913 | 6.178 | 10.39 | 11
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 17.6 | 0.11043 | 5.829 | 6.242 | 6.629 | 6.994 | 7.342 | 12.92 | 34
Bega | Quira | 66/11 | 5 |  |  | 0 | -0.054645 | 0.585 | 0.631 | 0.674 | 0.714 | 0.752 | 1.16 | 14
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 14.3 | 0.90645 | 0.782 | 0.837 | 0.888 | 0.937 | 0.983 | 1.55 | 26
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | -0.57106 | 0 | 0 | 0 | 0 | 0 | 0 | 608
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.64018 | 0.2 | 0.212 | 0.223 | 0.234 | 0.244 | 0.49 | 21
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 2.75 | -0.98894 | 0.689 | 0.721 | 0.752 | 0.781 | 0.809 | 1.46 | 12
Tumut | Batlow | 66/11 | 5 | 5 |  | 5.5 | 0.24254 | 0.685 | 0.723 | 0.759 | 0.793 | 0.826 | 1.34 | 28
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 8.8 | 0.98058 | 1.661 | 1.739 | 1.813 | 1.884 | 1.953 | 3.86 | 25
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.1 | -0.98172 | 0.35 | 0.376 | 0.4 | 0.423 | 0.444 | 0.55 | 11
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.81373 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.08 | 5
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | -0.88858 | 0.227 | 0.238 | 0.247 | 0.257 | 0.266 | 0.36 | 26
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 8.8 | 1 | 1.644 | 1.712 | 1.778 | 1.842 | 1.903 | 3.34 | 6
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 33 | 0.8779 | 3.65 | 3.859 | 4.057 | 4.247 | 4.428 | 7.62 | 10
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0 | 5.102 | 5.422 | 5.724 | 6.01 | 6.282 | 9.5 | 37
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 5.5 | 0.86938 | 1.928 | 2.054 | 2.173 | 2.286 | 2.393 | 3.57 | 36
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 11 | 0.70711 | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0 | 406
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 33 | 0 | 8.728 | 9.445 | 10.111 | 10.735 | 11.326 | 13.42 | 28
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 33 | 0.98619 | 5.281 | 5.665 | 6.024 | 6.363 | 6.685 | 9.56 | 13
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 33 | -0.98333 | 11.115 | 11.949 | 12.728 | 13.463 | 14.159 | 19.66 | 21
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 8.8 | 0.99 | 2.262 | 2.389 | 2.51 | 2.625 | 2.736 | 4.79 | 21
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 2.75 | -0.48269 | 1.238 | 1.315 | 1.387 | 1.456 | 1.522 | 2.62 | 21
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 20.9 | 0.98407 | 4.713 | 5.062 | 5.387 | 5.695 | 5.986 | 8.87 | 14
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0.819 | 1.946 | 2.042 | 2.135 | 2.223 | 2.308 | 4.61 | 7
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 33 | 0.87819 | 2.376 | 2.537 | 2.688 | 2.831 | 2.967 | 4.72 | 17
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.99879 | 0 | 0 | 0 | 0 | 0 | 0 | 115
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 16.5 | 0 | 4.885 | 5.184 | 5.466 | 5.733 | 5.989 | 8.54 | 17
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 16.5 | 0.99402 | 1.641 | 1.769 | 1.888 | 1.999 | 2.105 | 3.01 | 5
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.96754 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 15.4 | 0.97863 | 7.893 | 7.946 | 7.996 | 8.043 | 8.087 | 1.42 | 8212
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | -0.92968 | 0.841 | 0.876 | 0.91 | 0.942 | 0.974 | 1.44 | 3
Cowra | Canowindra | 66/11 | 5 | 8 |  | 5.5 | -0.85434 | 1.999 | 2.141 | 2.275 | 2.401 | 2.521 | 3.88 | 14
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 33 | 0.48043 | 8.44 | 9.001 | 9.529 | 10.029 | 10.505 | 12.74 | 24
Cowra | Grenfell | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 2.112 | 2.251 | 2.381 | 2.504 | 2.622 | 4.22 | 50
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.016391 | 0.261 | 0.269 | 0.277 | 0.284 | 0.292 | 0.68 | 27
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 5.5 | -0.8693 | 1.284 | 1.339 | 1.391 | 1.442 | 1.49 | 3.09 | 14
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 20.9 | -0.96152 | 8.414 | 8.7 | 8.97 | 9.224 | 9.466 | 7.8 | 14
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.15 | 0.96649 | 0.178 | 0.185 | 0.192 | 0.199 | 0.205 | 0.43 | 11
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 11 | -0.50488 | 1.784 | 1.894 | 1.998 | 2.097 | 2.192 | 3.94 | 6
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 33 | 0.1644 | 5.168 | 5.455 | 5.728 | 5.988 | 6.238 | 10.62 | 21
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 2.75 | 0.98638 | 0.566 | 0.6 | 0.633 | 0.664 | 0.693 | 1.31 | 28
Yass | Marilba | 66/11 | 3 |  |  | 0 | 0.99244 | 0.594 | 0.625 | 0.655 | 0.683 | 0.71 | 1.3 | 14
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | -0.98108 | 4.431 | 4.724 | 4.999 | 5.26 | 5.509 | 8.78 | 26
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 14.3 | -0.95242 | 5.136 | 5.418 | 5.686 | 5.942 | 6.188 | 10 | 13
Temora | Anona | 66/22 | 3 | 2.5 |  | 2.75 | -0.12201 | 0.444 | 0.465 | 0.485 | 0.504 | 0.523 | 0.99 | 3
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 2.75 | -0.85749 | 0.291 | 0.308 | 0.323 | 0.338 | 0.353 | 0.64 | 36
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.3 | -0.97855 | 0.312 | 0.331 | 0.35 | 0.367 | 0.383 | 0.74 | 47
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | -0.99796 | 0.132 | 0.133 | 0.134 | 0.135 | 0.135 | 0.17 | 11
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 11 | -0.97308 | 3.109 | 3.298 | 3.477 | 3.647 | 3.809 | 6.3 | 21
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 11 | 0.69905 | 2.819 | 2.953 | 3.081 | 3.205 | 3.323 | 5.63 | 26
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.3 | 0.99788 | 0.147 | 0.155 | 0.163 | 0.17 | 0.177 | 0.29 | 11
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 33 | 0.96511 | 0.583 | 0.584 | 0.585 | 0.586 | 0.587 | 0.3 | 13
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/10 | 6.75/10 |  | 11 | -0.98402 | 3.371 | 3.629 | 3.87 | 4.097 | 4.311 | 5.49 | 29
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 8.8 | -0.86924 | 1.939 | 2.056 | 2.167 | 2.272 | 2.372 | 4.35 | 29
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.3 | 0.80531 | 0.291 | 0.302 | 0.312 | 0.322 | 0.331 | 0.85 | 9
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 15.4 | 0.97927 | 1.499 | 1.601 | 1.696 | 1.786 | 1.871 | 2.75 | 11
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | -0.75974 | 0.136 | 0.144 | 0.152 | 0.159 | 0.167 | 0.24 | 5
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 16.5 | 0.27472 | 1.812 | 1.906 | 1.996 | 2.082 | 2.165 | 4.07 | 13
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | -0.9961 | 0 | 0 | 0 | 0 | 0 | 0 | 290
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.91358 | 0.16 | 0.166 | 0.172 | 0.178 | 0.184 | 0.39 | 22
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 7.59 | 0.91914 | 0.249 | 0.262 | 0.275 | 0.288 | 0.3 | 0.59 | 22
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.1 | 0.9 | 0.308 | 0.32 | 0.331 | 0.343 | 0.354 | 0.81 | 10
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 33 | 0.69253 | 5.925 | 6.408 | 6.857 | 7.278 | 7.676 | 11.61 | 18
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 14.63 | -0.99995 | 5.862 | 6.308 | 6.724 | 7.115 | 7.487 | 10.29 | 25
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 33 | 0.91767 | 1.876 | 1.967 | 2.055 | 2.138 | 2.219 | 5.1 | 13
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 5.5 | -0.95963 | 0.83 | 0.863 | 0.895 | 0.925 | 0.955 | 2.12 | 20
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 27.5 | -0.96393 | 6.625 | 7.101 | 7.547 | 7.969 | 8.369 | 13.19 | 23
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 5.5 | -0.62733 | 0.979 | 1.018 | 1.054 | 1.09 | 1.124 | 2.52 | 32
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 22 | 0.96835 | 1.015 | 1.08 | 1.141 | 1.198 | 1.253 | 2.82 | 23
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 17.6 | 0.61394 | 1.602 | 1.689 | 1.773 | 1.852 | 1.928 | 3.56 | 15
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 7.7 | -0.972 | 1.627 | 1.685 | 1.742 | 1.797 | 1.85 | 3.84 | 16
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 7.7 | -0.82748 | 1.247 | 1.3 | 1.351 | 1.401 | 1.449 | 3.2 | 12
Morven | Morven | 132/66 | 30 |  |  | 0 | -0.97897 | 2.84 | 2.95 | 3.056 | 3.158 | 3.257 | 0 | 36
Albury | Corowa | 132/22 | 30 | 27/30 |  | 33 | -0.93041 | 33.599 | 33.75 | 33.897 | 34.038 | 34.174 | 9.54 | 367
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 48.4 | 0.98525 | 7.716 | 8.24 | 8.732 | 9.199 | 9.642 | 18.28 | 9
Albury | Mulwala | 132/22 | 30 | 30 |  | 33 | -0.75496 | 16.678 | 17.07 | 17.442 | 17.796 | 18.134 | 7.66 | 14
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 77 | -0.97335 | 26.374 | 28.229 | 29.965 | 31.601 | 33.153 | 49.84 | 31
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 33 | 0 | 5.744 | 5.918 | 6.084 | 6.245 | 6.401 | 10.44 | 34
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 11 | -0.37139 | 0.939 | 0.973 | 1.005 | 1.037 | 1.068 | 2.34 | 28
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 11 | 0.73189 | 1.411 | 1.452 | 1.492 | 1.531 | 1.569 | 4.37 | 22
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 33 | 0.93633 | 6.23 | 6.607 | 6.963 | 7.302 | 7.625 | 12.7 | 57
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 5.5 | 0.99991 | 0.966 | 1 | 1.032 | 1.063 | 1.093 | 2.36 | 8
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 33 | -0.12404 | 4.465 | 4.736 | 4.993 | 5.236 | 5.469 | 9.39 | 24
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 5.5 | -0.34507 | 0.437 | 0.445 | 0.454 | 0.461 | 0.469 | 1.1 | 8
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 27.5 | 0.74266 | 5.327 | 5.337 | 5.348 | 5.358 | 5.369 | 0.41 | 154
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 8.25 | 0.49614 | 0.355 | 0.367 | 0.377 | 0.388 | 0.398 | 0.87 | 9
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 13.75 | 0.25909 | 0.734 | 0.764 | 0.792 | 0.819 | 0.846 | 1.31 | 18
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 2.75 | 0.61725 | 0.077 | 0.081 | 0.086 | 0.09 | 0.094 | 0.11 | 1
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.60616 | 0.325 | 0.332 | 0.339 | 0.346 | 0.352 | 0.51 | 80
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.65 | 0.87314 | 0.107 | 0.112 | 0.117 | 0.121 | 0.125 | 0.24 | 24
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 33 | 0.98796 | 0.635 | 0.643 | 0.651 | 0.659 | 0.667 | 1.1 | 22
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 11 | -0.95073 | 1.907 | 2.009 | 2.107 | 2.2 | 2.289 | 3.53 | 17
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 17.6 | 0.50998 | 2.564 | 2.696 | 2.822 | 2.942 | 3.058 | 3.82 | 13
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.1 | 0.50143 | 0.165 | 0.178 | 0.19 | 0.201 | 0.212 | 0.36 | 4
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 13.75 | -0.99904 | 3.754 | 4 | 4.232 | 4.452 | 4.661 | 6.32 | 8
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 55 | -0.17134 | 6.069 | 6.352 | 6.623 | 6.883 | 7.134 | 11.81 | 4
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 27.5 | 0.99577 | 0.855 | 0.873 | 0.891 | 0.909 | 0.926 | 2.18 | 7
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | -0.96011 | 0.365 | 0.375 | 0.384 | 0.393 | 0.402 | 0.61 | 2
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | -0.40082 | 4.628 | 4.864 | 5.089 | 5.304 | 5.511 | 8.28 | 4
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 2.75 | 0.68603 | 0.349 | 0.367 | 0.383 | 0.4 | 0.415 | 0.45 | 12
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.87872 | 0.258 | 0.28 | 0.3 | 0.318 | 0.336 | 0.36 | 11
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 10.45 | 0.78476 | 1.026 | 1.066 | 1.104 | 1.141 | 1.177 | 2.18 | 4
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.58106 | 0.098 | 0.105 | 0.112 | 0.118 | 0.124 | 0.15 | 19
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.69663 | 4.972 | 5.224 | 5.465 | 5.695 | 5.917 | 9.04 | 6
Yanco | Murrami | 33/11 | 5 | 5 |  | 5.5 | 0.25378 | 0.149 | 0.151 | 0.154 | 0.156 | 0.158 | 0.55 | 6
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.82382 | 7.194 | 7.307 | 7.416 | 7.521 | 7.621 | 5.72 | 20
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.7152 | 0.476 | 0.496 | 0.515 | 0.534 | 0.552 | 0.97 | 18
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.16758 | 0.872 | 0.92 | 0.966 | 1.009 | 1.051 | 1.87 | 4
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.89385 | 6.041 | 6.077 | 6.111 | 6.143 | 6.174 | 1.13 | 8
Buronga | Powercor Robinvale 22kV Euston Distribution Supply | [5 empty] | 0.97239 | 1.181 | 1.2 | 1.219 | 1.238 | 1.256 | 2.12 | 19
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply | [5 empty] | 0.709 | 0.553 | 0.56 | 0.567 | 0.574 | 0.581 | 1.33 | 6
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 33 | 0.66595 | 3.307 | 3.51 | 3.702 | 3.884 | 4.058 | 6.46 | 24
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 33 | -0.57179 | 4.915 | 5.066 | 5.208 | 5.343 | 5.471 | 4.75 | 33
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.8222 | 0.38 | 0.39 | 0.4 | 0.409 | 0.418 | 0.91 | 4
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Lines Export
Supply Area | Feeder # | Feeder Voltage kV | Feeder Origin | Feeder Destination
[5 empty] | Line Rating | Line Forecast POE50 MVA
[5 empty] | Summer MVA | 2025 | 2026 | 2027 | 2028 | 2029
Casino | 96L | 132 | Transgrid Casino 132kV 96L Tee | Casino ZS | 140 | 10.0054 | 10.5543 | 11.0751 | 11.5733 | 12.0499
Casino | 6501 | 66 | Casino ZS | Rappville Tee | 16 | 0.337 | 0.355 | 0.371 | 0.387 | 0.402
Casino | 8401 | 33 | Casino ZS | Mallanganee ZS | 4 | 0.999 | 1.0476 | 1.0935 | 1.1394 | 1.1826
Casino | 8402 | 33 | Mallanganee ZS | Bonalbo ZS | 4 | 0.697 | 0.73 | 0.762 | 0.794 | 0.824
Casino | 8403 | 33 | Bonalbo ZS | Urbenville ZS | 4 | 0.334 | 0.352 | 0.369 | 0.386 | 0.402
Coffs Harbour | 96C/2(D) | 132 | TransGrid 96C Armidale Coffs Harbour Dorrigo Tee | Dorrigo ZS | 41 | 1.923 | 2.024 | 2.119 | 2.211 | 2.299
Coffs Harbour | 702 | 66 | Boambee South 132/66kV STS | Sawtell ZS | 61 | 4.991 | 5.371 | 5.726 | 6.061 | 6.378
Coffs Harbour | 705 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 7.8458 | 8.3843 | 8.8901 | 9.3684 | 9.8237
Coffs Harbour | 706 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 8.9355 | 9.5488 | 10.1248 | 10.6695 | 11.1881
Coffs Harbour | 7501 | 66 | Nana Glen ZS | Woolgoolga ZS | 29 | 2.9266 | 3.1275 | 3.3161 | 3.4945 | 3.6644
Coffs Harbour | 7502 | 66 | Nana Glen ZS | Ulong Tee | 9 | 0.314 | 0.342 | 0.367 | 0.391 | 0.413
Coffs Harbour | 7502/1 | 66 | Ulong Tee | Ulong ZS | 9 | 0.314 | 0.342 | 0.367 | 0.391 | 0.413
Coffs Harbour | 7502/2 | 66 | Ulong Tee | Dorrigo ZS | 9 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | 7509 | 66 | Moonee ZS | Woolgoolga ZS | 30 | 8.407 | 8.989 | 9.535 | 10.052 | 10.543
Coffs Harbour | 7510 | 66 | North Coffs ZS | Moonee ZS | 61 | 3.7983 | 4.0591 | 4.3039 | 4.5355 | 4.7559
Coffs Harbour | 703:NGN | 66 | TransGrid Coffs Harbour 132/66 kV STS | Nana Glen ZS | 62 | 4.7946 | 5.1237 | 5.4328 | 5.7251 | 6.0034
Coffs Harbour | 711:CHN | 66 | TransGrid Coffs Harbour 132/66 kV STS | North Coffs ZS | 62 | 9.6515 | 10.314 | 10.9362 | 11.5246 | 12.0847
Coffs Harbour | 87C | 66 | North Coffs ZS | South Coffs ZS | 68 | 6.04 | 6.4546 | 6.8439 | 7.2121 | 7.5627
Grafton | 825 | 66 | TransGrid Koolkhan 132/66kV STS | Koolkhan ZS | 62 | 10.3285 | 10.9156 | 11.4726 | 12.004 | 12.5125
Grafton | 826 | 66 | TransGrid Koolkhan 132/66kV STS | Grafton North ZS | 61 | 8.4274 | 8.9064 | 9.3608 | 9.7945 | 10.2094
Grafton | 6503 | 66 | Grafton North ZS | South Grafton ZS | 24 | 5.5047 | 5.8177 | 6.1145 | 6.3977 | 6.6688
Grafton | 6504 | 66 | Five Mile Sw Stn | South Grafton ZS | 61 | 2.3835 | 2.519 | 2.6475 | 2.7702 | 2.8875
Grafton | 6505 | 66 | Koolkhan SS | Grafton ZS | 52 | 9.1651 | 9.6861 | 10.1803 | 10.6519 | 11.1031
Grafton | 6506 | 66 | Shannon Creek ZS | Nymboida ZS | 14 | 0.14188 | 0.14994 | 0.15759 | 0.16489 | 0.17188
Grafton | 6508 | 66 | Maclean ZS | Yamba ZS | 28 | 6.876 | 7.32 | 7.739 | 8.136 | 8.514
Grafton | 6509 | 66 | Shannon Creek ZS | Five Mile Sw Stn | 14 | 0.65263 | 0.68972 | 0.72491 | 0.75849 | 0.79063
Grafton | 6510 | 66 | Grafton North ZS | Five Mile Sw Stn | 28 | 2.9794 | 3.1487 | 3.3094 | 3.4627 | 3.6094
Grafton | 896:MLN | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 21 | 4.9089 | 5.1879 | 5.4526 | 5.7052 | 5.9469
Grafton | 8G1 | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 68 | 6.2992 | 6.6573 | 6.997 | 7.3211 | 7.6312
Grafton | 6402 | 33 | Maclean ZS | Yamba Tee | 8 | 0.25538 | 0.26989 | 0.28366 | 0.2968 | 0.30938
Grafton | 6403 | 33 | Yamba Tee | Redcliff ZS | 3 | 0.25538 | 0.26989 | 0.28366 | 0.2968 | 0.30938
Grafton | 6404 | 33 | Yamba Tee | Yamba ZS | 10 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7Y1 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 2.2794 | 2.4139 | 2.541 | 2.6625 | 2.7787
Hawks Nest | 7Y2 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 2.0906 | 2.2139 | 2.3305 | 2.4419 | 2.5485
Hawks Nest | 7V1 | 33 | Ausgrid Salt Ash ZS | Tee with 7Y1 | 7 | 0 | 0 | 0 | 0 | 0
Herons Creek | 866:KEW | 66 | Herons Creek 132/66kV STS | Kew ZS | 16 | 6.943 | 7.347 | 7.729 | 8.094 | 8.442
Herons Creek | 871 | 66 | Kew ZS | Laurieton ZS | 36 | 4.669 | 4.95 | 5.215 | 5.468 | 5.709
Herons Creek | 862/1 | 66 | Kew ZS | Johns River ZS | 16 | 0.327 | 0.34 | 0.352 | 0.364 | 0.376
Herons Creek | 862/2 | 66 | TransGrid Taree 132/66/33kV STS | Johns River ZS | 16 | 0 | 0 | 0 | 0 | 0
Kempsey | 7R1 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 30 | 3.4999 | 3.7388 | 3.9637 | 4.1764 | 4.3788
Kempsey | 7R2/1 | 33 | TransGrid Kempsey 132/33kV STS | North St Tee | 26 | 4.0509 | 4.3275 | 4.5878 | 4.834 | 5.0682
Kempsey | 7R2/2 | 33 | North St Tee | Smithtown ZS | 19 | 2.0254 | 2.1638 | 2.2939 | 2.417 | 2.5341
Kempsey | 7R2/3 | 33 | North St Tee | North St ZS | 10 | 1.9957 | 2.1319 | 2.2602 | 2.3814 | 2.4968
Kempsey | 7R3 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 26 | 3.5147 | 3.7548 | 3.9806 | 4.1942 | 4.3974
Kempsey | 7R4 | 33 | TransGrid Kempsey 132/33kV STS | Munga ZS | 3 | 0.661 | 0.696 | 0.73 | 0.762 | 0.793
Kempsey | 7R5 | 33 | TransGrid Kempsey 132/33kV STS | North St ZS | 19 | 3.068 | 3.2775 | 3.4746 | 3.661 | 3.8384
Kempsey | 7R6/1 | 33 | Prince St ZS | South West Rocks Tee | 15 | 2.5616 | 2.7365 | 2.9011 | 3.0568 | 3.2049
Kempsey | 7R6/2 | 33 | South West Rocks Tee | South West Rocks ZS | 19 | 1.2957 | 1.3842 | 1.4674 | 1.5462 | 1.6211
Kempsey | 7R6/3 | 33 | South West Rocks Tee | Smithtown ZS | 19 | 1.2063 | 1.2887 | 1.3662 | 1.4395 | 1.5093
Kempsey | 7R7 | 33 | Prince St ZS | Crescent Head ZS | 5 | 0.928 | 0.987 | 1.044 | 1.097 | 1.149
Kempsey | 7R8 | 33 | Smithtown ZS | South West Rocks ZS | 30 | 1.534 | 1.6387 | 1.7373 | 1.8305 | 1.9192
Lismore | 9U8 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 183 | 25.3176 | 26.2316 | 27.0982 | 27.9243 | 28.7142
Lismore | 9U9 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 23.4292 | 24.2751 | 25.0771 | 25.8416 | 26.5725
Lismore | 9W1 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 21.6808 | 22.4635 | 23.2057 | 23.9131 | 24.5895
Lismore | 9G2 | 132 | Ballina ZS | Lennox Head ZS | 124 | 5.595 | 5.797 | 5.9886 | 6.1711 | 6.3457
Lismore | 9G3 | 132 | Lennox Head ZS | Suffolk Park ZS | 124 | 7.4834 | 7.7535 | 8.0097 | 8.2539 | 8.4873
Lismore | 9G4 | 132 | Suffolk Park ZS | Ewingsdale ZS | 124 | 10.4208 | 10.797 | 11.1537 | 11.4937 | 11.8188
Lismore | 9G5 | 132 | Ewingsdale ZS | Mullumbimby ZS | 122 | 18.1839 | 18.8404 | 19.4628 | 20.0561 | 20.6235
Lismore | 9U6 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 33.5702 | 34.7822 | 35.9314 | 37.0267 | 38.0741
Lismore | 9U6/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 27.2758 | 28.2606 | 29.1942 | 30.0842 | 30.9352
Lismore | 9U7 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 34.969 | 36.2315 | 37.4285 | 38.5695 | 39.6605
Lismore | 9U7/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 28.6746 | 29.7098 | 30.6914 | 31.627 | 32.5216
Lismore | 892 | 66 | Lismore 132/66kV STS | Woodburn ZS | 11 | 4.058 | 4.29 | 4.51 | 4.72 | 4.921
Lismore | 893 | 66 | Lismore 132/66kV STS | Casino ZS | 34 | 0 | 0 | 0 | 0 | 0
Lismore | 894:LME | 66 | Lismore 132/66kV STS | Kyogle ZS | 11 | 3.356 | 3.525 | 3.687 | 3.842 | 3.991
Lismore | 0897:LME | 66 | Lismore 132/66kV STS | Alstonville ZS | 62 | 8.8821 | 9.2028 | 9.5068 | 9.7967 | 10.0738
Lismore | 8502 | 66 | Lismore East ZS | Alstonville ZS | 62 | 4.6858 | 4.855 | 5.0154 | 5.1683 | 5.3145
Lismore | 8503 | 66 | Ballina ZS | Alstonville ZS | 62 | 4.1263 | 4.2753 | 4.4166 | 4.5512 | 4.6799
Lismore | 8507 | 66 | Alstonville ZS | Ballina ZS | 61 | 4.7558 | 4.9275 | 5.0903 | 5.2455 | 5.3938
Lismore | 8510 | 66 | Lismore Sw Stn | East Lismore ZS | 61 | 10.7005 | 11.0868 | 11.4531 | 11.8023 | 12.1361
Lismore | 8511 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 9.3717 | 9.71 | 10.0308 | 10.3366 | 10.629
Lismore | 8512 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 4.1035 | 4.35 | 4.5835 | 4.8055 | 5.0175
Lismore | 8513 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 4.1035 | 4.35 | 4.5835 | 4.8055 | 5.0175
Lismore | 8514 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 1.632 | 1.7245 | 1.812 | 1.8955 | 1.9755
Lismore | 8515 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 1.5353 | 1.6276 | 1.7149 | 1.7983 | 1.8782
Lismore | 8516 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 9.3018 | 9.6376 | 9.956 | 10.2595 | 10.5497
Nambucca Heads | 751 | 66 | TransGrid Nambucca 132/66 kV STS | Nambucca ZS | 15 | 4.485 | 4.788 | 5.072 | 5.341 | 5.598
Port Macquarie | 70Y | 33 | Rocks Ferry ZS | Telegraph Point ZS | 8 | 0.891 | 0.948 | 1.001 | 1.052 | 1.101
Port Macquarie | 701 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 22 | 6.1164 | 6.5493 | 6.9553 | 7.3388 | 7.7034
Port Macquarie | 703:BPM | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 5.0691 | 5.4278 | 5.7643 | 6.0822 | 6.3843
Port Macquarie | 707 | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 5.7393 | 6.1455 | 6.5265 | 6.8864 | 7.2285
Port Macquarie | 708 | 33 | TransGrid Port Macquarie 132/33kV STS | Owen Street ZS | 26 | 6.661 | 7.1324 | 7.5746 | 7.9923 | 8.3893
Port Macquarie | 710 | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 31 | 7.2475 | 7.7604 | 8.2415 | 8.696 | 9.128
Port Macquarie | 711:CPM | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 20 | 7.2056 | 7.7156 | 8.1939 | 8.6458 | 9.0752
Port Macquarie | 712 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 12 | 4.0636 | 4.3512 | 4.621 | 4.8758 | 5.118
Port Macquarie | 715 | 33 | Clearwater ZS | Owen Street ZS | 31 | 3.0163 | 3.2298 | 3.43 | 3.6192 | 3.7989
Port Macquarie | 719/1 | 33 | Clearwater ZS | Lake Cathie ZS | 20 | 5.321 | 5.694 | 6.045 | 6.376 | 6.69
Port Macquarie | 719/2 | 33 | Lake Cathie ZS | Laurieton ZS | 12 | 0 | 0 | 0 | 0 | 0
Port Macquarie | 765 | 33 | Rocks Ferry ZS | Koree ZS | 9 | 2.723 | 2.9158 | 3.0965 | 3.2673 | 3.4296
Port Macquarie | 784 | 33 | Koree ZS | Byabarra ZS | 9 | 0.71218 | 0.76259 | 0.80986 | 0.85452 | 0.89697
Stroud | 9C9/3 | 33 | Stroud 132/33kV STS | Dungog ZS | 27 | 2.7833 | 2.9442 | 3.0959 | 3.2401 | 3.3789
Stroud | 9C9/2 | 33 | Dungog ZS | Martins Creek ZS | 21 | 2.24 | 2.359 | 2.472 | 2.579 | 2.683
Stroud | STR4B3/1 | 33 | Stroud 132/33kV STS | Booral ZS | 7 | 1.8682 | 1.9785 | 2.0831 | 2.1825 | 2.2776
Stroud | STR4B3/2 | 33 | Booral ZS | Bulahdelah ZS | 7 | 1.3403 | 1.4194 | 1.4944 | 1.5657 | 1.6339
Stroud | STR4B4 | 33 | Stroud 132/33kV STS | Dungog ZS | 4 | 0.96346 | 1.0191 | 1.0716 | 1.1216 | 1.1696
Stroud | STR4B5/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 2.6534 | 2.8101 | 2.9586 | 3.0997 | 3.2348
Stroud | STR4B5/2 | 33 | Wards River Sw Stn | Stratford Tee | 19 | 1.4026 | 1.4831 | 1.5586 | 1.6301 | 1.6983
Stroud | STR4B5/2a | 33 | Stratford Tee | Stratford Coal ZS | 7 | 0 | 0 | 0 | 0 | 0
Stroud | STR4B5/3 | 33 | Stratford Tee | Gloucester ZS | 19 | 1.1883 | 1.2696 | 1.3457 | 1.4178 | 1.4865
Stroud | STR4B6/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 3.0596 | 3.2402 | 3.4115 | 3.5742 | 3.7299
Stroud | STR4B6/2 | 33 | Wards River Sw Stn | Gloucester ZS | 17 | 2.3067 | 2.4644 | 2.6123 | 2.7522 | 2.8855
Stroud | STR4B7 | 33 | Stroud 132/33kV STS | Dungog ZS | 7 | 1.4452 | 1.5287 | 1.6075 | 1.6824 | 1.7544
Stroud | STR4B8 | 33 | Stroud 132/33kV STS | Bulahdelah ZS | 7 | 1.6923 | 1.7921 | 1.8869 | 1.9769 | 2.063
Stroud | 3801 | 33 | Bulahdelah ZS | Pacific Palms ZS | 7 | 1.866 | 1.985 | 2.098 | 2.205 | 2.308
Stroud | 3803 | 33 | Bulahdelah ZS | Bungwahl Sw Stn | 7 | 0 | 0 | 0 | 0 | 0
Stroud | BLH4B4 | 33 | Bulahdelah ZS | Hawks Nest 132/33kV STS | 7 | 0.094766 | 0.10036 | 0.10566 | 0.1107 | 0.11553
Stroud | 7J1 | 33 | Ausgrid Recloser 33175 (Patterson) | Martins Creek Tee | 8 | 0 | 0 | 0 | 0 | 0
Stroud | 7J1/2 | 33 | Martins Creek Tee | Martins Creek ZS | 4 | 0.864 | 0.912 | 0.957 | 1 | 1.041
Stroud | 7J1/3 | 33 | Martins Creek Tee | Gresford ZS | 4 | 0.864 | 0.912 | 0.957 | 1 | 1.041
Taree | 861 | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 4.9278 | 5.2841 | 5.618 | 5.9331 | 6.2322
Taree | 863:WTE | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 5.1047 | 5.4738 | 5.8196 | 6.1461 | 6.4559
Taree | 867 | 66 | TransGrid Taree 132/66/33kV STS | Hallidays Point ZS | 34 | 6.9243 | 7.4249 | 7.8939 | 8.3367 | 8.757
Taree | 867/1 | 66 | Hallidays Point Tee | Tuncurry ZS | 39 | 6.9243 | 7.4249 | 7.8939 | 8.3367 | 8.757
Taree | 868/1 | 66 | TransGrid Taree 132/66/33kV STS | Bohnock Tee | 36 | 8.112 | 8.6985 | 9.248 | 9.7667 | 10.2592
Taree | 868/2 | 66 | Bohnock Tee | Bohnock ZS | 16 | 4.269 | 4.591 | 4.893 | 5.176 | 5.445
Taree | 868/3 | 66 | Bohnock Tee | Hallidays Point ZS | 38 | 5.9387 | 6.368 | 6.7703 | 7.1501 | 7.5106
Taree | 872 | 66 | Tuncurry ZS | Forster ZS | 30 | 3.4874 | 3.7395 | 3.9758 | 4.1988 | 4.4105
Taree | 86C | 66 | Tuncurry ZS | Forster ZS | 42 | 3.0578 | 3.2789 | 3.486 | 3.6815 | 3.8672
Taree | 86R | 66 | Hallidays Point ZS | Tuncurry ZS | 38 | 5.8123 | 6.2325 | 6.6263 | 6.998 | 7.3508
Taree | 7G2/1 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Tee | 22 | 1.868 | 1.9868 | 2.0989 | 2.2053 | 2.3067
Taree | 7G2/2 | 33 | Kanangra Tee | Coopernook ZS | 7 | 1.5974 | 1.699 | 1.7949 | 1.8858 | 1.9726
Taree | 7G2/3 | 33 | Coopernook ZS | Harrington ZS | 8 | 2.969 | 3.17 | 3.359 | 3.538 | 3.709
Taree | 7G4 | 33 | Bootawa ZS | Wingham ZS | 18 | 0.74196 | 0.78914 | 0.83368 | 0.87592 | 0.91622
Taree | 7G5 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Dr ZS | 17 | 2.7496 | 2.9245 | 3.0895 | 3.2461 | 3.3954
Taree | 7G1 | 33 | TransGrid Taree 132/66/33kV STS | Bootawa ZS | 17 | 2.0077 | 2.1353 | 2.2558 | 2.3702 | 2.4792
Taree | 7G3 | 33 | TransGrid Taree 132/66/33kV STS | Wingham ZS | 18 | 2.1124 | 2.2467 | 2.3735 | 2.4938 | 2.6085
Terranora | 757 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 141.4214
Terranora | 758 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 142.8356
Terranora | 9501 | 66 | Terranora 110/66kV STS | Cudgen ZS | 59 | 7.8435 | 8.2755 | 8.6868 | 9.0783 | 9.4545
Terranora | 9502 | 66 | Terranora 110/66kV STS | Murwillumbah ZS | 61 | 5.345 | 5.634 | 5.9095 | 6.172 | 6.4245
Terranora | 9503 | 66 | Terranora 110/66kV STS | Banora Pt ZS | 59 | 14.875 | 15.6905 | 16.4668 | 17.2074 | 17.9165
Terranora | 9504 | 66 | Terranora 110/66kV STS | Condong Sw Stn | 61 | 4.8105 | 5.0706 | 5.3186 | 5.5548 | 5.782
Terranora | 9505 | 66 | Cudgen ZS | Banora Point ZS | 53 | 0.6066 | 0.63974 | 0.67129 | 0.70138 | 0.73023
Terranora | 9508 | 66 | Terranora 110/66kV STS | Tweed Heads ZS | 41 | 2.9726 | 3.1437 | 3.3064 | 3.4608 | 3.6088
Terranora | 9510 | 66 | Banora Point ZS | Tweed Heads South ZS | 43 | 9.2883 | 9.7934 | 10.2732 | 10.732 | 11.1709
Terranora | 9514 | 66 | Condong Sw Stn | Murwillumbah ZS | 61 | 9.0865 | 9.5778 | 10.0462 | 10.4924 | 10.9216
Terranora | 9516 | 66 | Tweed Head South ZS | Tweed Heads ZS | 43 | 0.70775 | 0.7485 | 0.78725 | 0.824 | 0.85925
Terranora | 9406 | 33 | Cudgen ZS | Casuarina Sw Stn | 17 | 9.114 | 9.621 | 10.102 | 10.561 | 11.001
Terranora | 9407 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 0 | 0 | 0 | 0 | 0
Terranora | 9409 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 9.114 | 9.621 | 10.102 | 10.561 | 11.001
Armidale | 661/1 | 66 | TransGrid Armidale 330/132/66kV STS | Hillgrove Tee | 20 | 0.58349 | 0.61233 | 0.63955 | 0.66539 | 0.69006
Armidale | 661/2 | 66 | Hillgrove Tee | Hillgrove ZS | 16 | 0.25007 | 0.26243 | 0.27409 | 0.28517 | 0.29574
Armidale | 661/3 | 66 | Hillgrove Tee | Oaky ZS | 20 | 0.35426 | 0.37177 | 0.3883 | 0.40399 | 0.41896
Armidale | 662/1 | 66 | TransGrid Armidale 330/132/66kV STS | Uralla Tee | 12 | 2.887 | 3.045 | 3.196 | 3.341 | 3.479
Armidale | 662/2 | 66 | Uralla Tee | Uralla ZS | 9 | 1.82 | 1.935 | 2.044 | 2.148 | 2.247
Armidale | 662/4 | 66 | Uralla Tee | Walcha South ZS | 9 | 1.067 | 1.11 | 1.152 | 1.193 | 1.232
Armidale | 664 | 66 | TransGrid Armidale 330/132/66kV STS | Galloway St ZS | 28 | 9.6276 | 10.1035 | 10.5525 | 10.979 | 11.386
Armidale | 665 | 66 | TransGrid Armidale 330/132/66kV STS | Madgwick Dr ZS | 21 | 6.1892 | 6.4951 | 6.7838 | 7.0579 | 7.3196
Armidale | 66C | 66 | Miller St ZS | Madgwick Dr ZS | 21 | 1.2295 | 1.2903 | 1.3476 | 1.4021 | 1.4541
Armidale | 66F | 66 | Galloway St ZS | Miller St ZS | 15 | 4.4179 | 4.6362 | 4.8423 | 5.038 | 5.2247
Bathurst | 81H | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 62 | 3.6019 | 3.8606 | 4.103 | 4.3319 | 4.5494
Bathurst | 81G | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 64 | 5.1456 | 5.5152 | 5.8614 | 6.1884 | 6.4992
Bathurst | 81F | 66 | TransGrid Panorama 132/66kV STS | Russell St ZS | 64 | 8.7033 | 9.3534 | 9.962 | 10.5352 | 11.0786
Bathurst | 81J | 66 | Raglan ZS | Russell St ZS | 64 | 1.6639 | 1.7881 | 1.9045 | 2.0141 | 2.118
Bathurst | 81L | 66 | TransGrid Panorama 132/66kV STS | Raglan ZS | 64 | 5.3756 | 5.7771 | 6.153 | 6.5071 | 6.8426
Bathurst | 81C | 66 | TransGrid Panorama 132/66kV STS | Blayney ZS | 25 | 4.2903 | 4.5959 | 4.8804 | 5.1513 | 5.4085
Bathurst | 66:MAN | 66 | Blayney ZS | Mandurama ZS | 9 | 0.91 | 0.957 | 1.001 | 1.044 | 1.086
Beryl | 94M/4 | 132 | TransGrid 94M Mudgee Tee | Mudgee ZS | 128 | 8.668 | 9.208 | 9.718 | 10.202 | 10.665
Beryl | 851/1 | 66 | TransGrid Beryl 132/66kV STS | Gulgong ZS | 28 | 1.121 | 1.195 | 1.264 | 1.33 | 1.393
Beryl | 851/2 | 66 | Gulgong ZS | Mudgee ZS | 28 | 0 | 0 | 0 | 0 | 0
Beryl | 852 | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 15 | 0 | 0 | 0 | 0 | 0
Beryl | 86J | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 61 | 4.643 | 4.842 | 5.035 | 5.219 | 5.397
Beryl | 85A | 66 | Dunedoo ZS | Coonabarabran ZS | 11 | 3.4257 | 3.5299 | 3.6312 | 3.7279 | 3.8217
Beryl | 80L | 66 | Ulan Sw Stn | Ulan Town ZS | 15 | 0.874 | 0.913 | 0.951 | 0.987 | 1.022
Beryl | 80R | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 64 | 0 | 0 | 0 | 0 | 0
Beryl | 80U | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 61 | 0 | 0 | 0 | 0 | 0
Beryl | 80T | 66 | Ulan Sw Stn | Moolarben No1 Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Beryl | 80W | 66 | Moolarben No1 Mine ZS | Moolarben No2 Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Beryl | 80X | 66 | Moolarben No2 Mine ZS | Wilpinjong Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Broken Hill | X4 | 220 | TransGrid Broken Hill 220/22kV STS | Perilya Mine | 213 | 0 | 0 | 0 | 0 | 0
Broken Hill | 5B1:PPL | 66 | Pinnacles Place ZS | Mt Gipps ZS | 19 | 0 | 0 | 0 | 0 | 0
Broken Hill | 5B1:MTG | 66 | Mt Gipps ZS | Sunset Strip ZS | 19 | 0.378 | 0.381 | 0.385 | 0.388 | 0.391
Broken Hill | 5B1:SUN | 66 | Sunset Strip ZS | Menindee ZS | 6 | 0.492 | 0.523 | 0.551 | 0.578 | 0.604
Dubbo | 94J/3 | 132 | 94J Tee | Dubbo South ZS | 106 | 21.473 | 22.1499 | 22.7924 | 23.4051 | 23.9916
Dubbo | 943/2 | 132 | Dubbo South ZS | Narromine South Sw Stn | 106 | 15.266 | 15.7472 | 16.204 | 16.6395 | 17.0565
Dubbo | 94W/1 | 132 | Dubbo 132/66kV STS | Nevertire Tee | 128 | 143.8931 | 143.8447 | 143.7984 | 143.7542 | 143.7108
Dubbo | 94W/2 | 132 | Nevertire Tee | Nevertire ZS | 124 | 1.51 | 1.579 | 1.645 | 1.708 | 1.77
Dubbo | 94W/3 | 132 | Nevertire Tee | Nevertire Sw Stn | 128 | 144.9569 | 144.9569 | 144.9569 | 144.9569 | 144.9569
Dubbo | 9GX | 132 | Nevertire Sw Stn | Nyngan 132/66kV STS | 128 | 4.2792 | 4.5408 | 4.788 | 5.0224 | 5.2464
Dubbo | 9GP | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 12.995 | 13.177 | 13.352 | 13.519 | 13.681
Dubbo | 9GR | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GT | 132 | Dubbo West ZS | Narromine South Sw Stn | 140 | 18.344 | 18.853 | 19.337 | 19.797 | 20.239
Dubbo | 9GU | 132 | Narromine South Sw Stn | Nyngan 132/66kV STS | 106 | 11.7678 | 12.4872 | 13.167 | 13.8116 | 14.4276
Dubbo | 9GW | 132 | Dubbo 132/66kV STS | Dubbo West ZS | 140 | 16.608 | 17.1316 | 17.6285 | 18.1023 | 18.556
Dubbo | 812 | 66 | Yarrandale ZS | Gilgandra ZS | 15 | 0 | 0 | 0 | 0 | 0
Dubbo | 815 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 1.5415 | 1.6315 | 1.717 | 1.7985 | 1.8765
Dubbo | 816 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 1.5415 | 1.6315 | 1.717 | 1.7985 | 1.8765
Dubbo | 813:EUL | 66 | Eulomogo ZS | Geurie Tee | 12 | 0.598 | 0.639 | 0.677 | 0.714 | 0.748
Dubbo | 813/1:GUE | 66 | Geurie Tee | Geurie ZS | 16 | 0.598 | 0.639 | 0.677 | 0.714 | 0.748
Dubbo | 814/1 | 66 | Gilgandra ZS | Gulargambone ZS | 11 | 2.2782 | 2.3861 | 2.49 | 2.5899 | 2.6849
Dubbo | 814/2 | 66 | Gulargambone ZS | Coonamble ZS | 11 | 1.741 | 1.829 | 1.913 | 1.994 | 2.071
Dubbo | 81M | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 6.728 | 7.013 | 7.2825 | 7.539 | 7.784
Dubbo | 81P | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 61 | 2.5288 | 2.6502 | 2.7667 | 2.8783 | 2.9849
Dubbo | 81R | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 6.728 | 7.013 | 7.2825 | 7.539 | 7.784
Dubbo | 81X | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 28 | 3.0908 | 3.2392 | 3.3815 | 3.5179 | 3.6482
Dubbo | 81T | 66 | Yarrandale ZS | Gilgandra ZS | 43 | 4.5734 | 4.7902 | 4.999 | 5.1988 | 5.3897
Forbes | 858 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 3.997 | 4.227 | 4.446 | 4.655 | 4.854
Forbes | 859 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 0 | 0 | 0 | 0 | 0
Forbes | 893/5 | 66 | TransGrid Forbes 132/66kV STS | Payten's Bridge ZS | 12 | 0.568 | 0.595 | 0.621 | 0.646 | 0.669
Forbes | 894:CDN | 66 | Condobolin ZS | Lake Cargelligo ZS | 15 | 1.326 | 1.368 | 1.408 | 1.448 | 1.486
Forbes | 896:WJL | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 20 | 25.4558 | 25.4558 | 25.4558 | 25.4558 | 25.4558
Forbes | 897:CDN | 66 | West Jemalong ZS | Condobolin ZS | 20 | 2.7942 | 2.9235 | 3.0474 | 3.1664 | 3.2813
Forbes | 89H | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 43 | 42.4264 | 42.4264 | 42.4264 | 42.4264 | 42.4264
Glen Innes | 886 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 70 | 2.7452 | 2.8869 | 3.0221 | 3.151 | 3.2753
Glen Innes | 887 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 19 | 3.2678 | 3.4364 | 3.5975 | 3.7509 | 3.8988
Glen Innes | 6NY | 66 | Glen Innes ZS | Guyra ZS | 11 | 1.839 | 1.936 | 2.028 | 2.116 | 2.201
Glen Innes | 6NE | 66 | Glen Innes ZS | Emmaville ZS | 17 | 0.55264 | 0.58116 | 0.6084 | 0.63434 | 0.65936
Glen Innes | 6AE/A | 66 | Pindari ZS | Ashford ZS | 17 | 0 | 0 | 0 | 0 | 0
Glen Innes | 6AE/E | 66 | Emmaville ZS | Pindari ZS | 17 | 0.19222 | 0.20214 | 0.21162 | 0.22064 | 0.22934
Gunnedah | 877 | 66 | TransGrid Gunnedah 132/66kV STS | Keepit Dam ZS | 10 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 0.28284
Gunnedah | 88G/1 | 66 | Gunnedah ZS | Emerald Hill Sw Stn | 24 | 17.5177 | 17.5395 | 17.56 | 17.5804 | 17.6002
Gunnedah | 88G/2 | 66 | Emerald Hill Sw Stn | Boggabri ZS | 24 | 0.762 | 0.792 | 0.82 | 0.848 | 0.875
Gunnedah | 88K | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 11.9029 | 12.172 | 12.4252 | 12.6658 | 12.8954
Gunnedah | 88L | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 11.9029 | 12.172 | 12.4252 | 12.6658 | 12.8954
Inverell | 734 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 5.7809 | 6.0378 | 6.2838 | 6.5204 | 6.7491
Inverell | 735 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 5.8741 | 6.1352 | 6.3852 | 6.6256 | 6.8579
Inverell | 6AB | 66 | Borthwick St ZS | Ashford ZS | 17 | 2.1096 | 2.2033 | 2.2931 | 2.3794 | 2.4629
Inverell | 6AF/A | 66 | Ashford ZS | Wallangra ZS | 11 | 0.29137 | 0.30433 | 0.31672 | 0.32865 | 0.34018
Inverell | 6AF/F | 66 | Wallangra ZS | Coolatai Sw Stn | 11 | 0.24476 | 0.25563 | 0.26605 | 0.27607 | 0.28575
Inverell | 6AX | 66 | Ashford ZS | Texas ZS | 9 | 1.7599 | 1.8381 | 1.913 | 1.985 | 2.0547
Inverell | 6BC | 66 | Borthwick St ZS | Copeton ZS | 21 | 0.26806 | 0.27998 | 0.29139 | 0.30236 | 0.31296
Inverell | 6BD | 66 | Borthwick St ZS | Bundarra ZS | 14 | 0.30303 | 0.3165 | 0.32939 | 0.3418 | 0.35378
Inverell | 6BW | 66 | Borthwick St ZS | Warialda ZS | 15 | 2.3193 | 2.4224 | 2.5211 | 2.6161 | 2.7078
Inverell | 6FH | 66 | Coolatai Sw Stn | Yallaroi ZS | 20 | 0.73426 | 0.7669 | 0.79815 | 0.8282 | 0.85724
Inverell | 6FW | 66 | Warialda ZS | Coolatai Sw Stn | 11 | 0.55944 | 0.5843 | 0.60811 | 0.63101 | 0.65314
Inverell | 6HG | 66 | Yallaroi ZS | Goondiwindi ZS | 20 | 0 | 0 | 0 | 0 | 0
Inverell | 6WK | 66 | Warialda ZS | Bingara ZS | 11 | 0.89743 | 0.93732 | 0.97551 | 1.0122 | 1.0477
Molong | 8C1 | 66 | TransGrid Molong 132/66kV STS | Cumnock / Orange West Tee | 61 | 0.57 | 0.592 | 0.613 | 0.633 | 0.653
Molong | 8C1/3 | 66 | Cumnock / Orange West Tee | Cumnock ZS | 9 | 0.57 | 0.592 | 0.613 | 0.633 | 0.653
Molong | 8C1/4 | 66 | Cumnock / Orange West Tee | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0
Moree | 876 | 66 | TransGrid Moree 132/66kV STS | Moree Solar Farm | 70 | 0.161 | 0.163 | 0.165 | 0.167 | 0.169
Moree | 87J | 66 | Moree Solar Farm | Bellata ZS | 25 | 0.161 | 0.163 | 0.165 | 0.167 | 0.169
Moree | 721 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 5.6774 | 5.788 | 5.8952 | 5.9985 | 6.0983
Moree | 722 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 5.9879 | 6.1046 | 6.2176 | 6.3265 | 6.4318
Moree | 881/1 | 66 | TransGrid Moree 132/66kV STS | Ashley Tee | 15 | 0.94442 | 0.96691 | 0.98845 | 1.009 | 1.0286
Moree | 881/2 | 66 | Ashley Tee | Ashley ZS | 10 | 0.228 | 0.231 | 0.234 | 0.237 | 0.239
Moree | 6PU | 66 | Ashley Tee | Mungindi ZS | 10 | 0.495 | 0.515 | 0.534 | 0.552 | 0.57
Moree | 723:WTR/1 | 66 | TransGrid Moree 132/66kV STS | Wathagar ZS | 12 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Moree | 723:WTR/2 | 66 | Wathagar ZS | Wenna ZS | 15 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Narrabri | 879 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 18 | 0.6606 | 0.68904 | 0.7164 | 0.74268 | 0.76824
Narrabri | 882 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 64 | 1.2845 | 1.3398 | 1.393 | 1.4441 | 1.4938
Narrabri | 885 | 66 | Burren Junction ZS | Merrywinebone ZS | 15 | 0.275 | 0.292 | 0.309 | 0.324 | 0.339
Narrabri | 833:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 2.2495 | 2.337 | 2.421 | 2.502 | 2.581
Narrabri | 834:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 2.2495 | 2.337 | 2.421 | 2.502 | 2.581
Narrabri | 861/1 | 66 | TransGrid Narrabri 132/66kV STS | Wilga Park ZS | 64 | 36.4888 | 36.2385 | 36.0024 | 35.7789 | 35.5674
Narrabri | 861/2 | 66 | Wilga Park ZS | Walgett ZS | 64 | 3.1416 | 3.3611 | 3.5669 | 3.7601 | 3.9449
Narrabri | 88F | 66 | Narrabri Sw Stn | Boggabri ZS | 24 | 0 | 0 | 0 | 0 | 0
Narrabri | 878/3 | 66 | TransGrid Narrabri 132/66kV STS | Narrabri Sw Stn | 61 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 26.4458
Narrabri | 88C | 66 | Narrabri Sw Stn | Narrabri Coal | 53 | 26.163 | 26.163 | 26.163 | 26.163 | 26.163
Narrabri | 880/1 | 66 | Wee Waa ZS | Burren Junction ZS | 13 | 0.5265 | 0.549 | 0.5706 | 0.5913 | 0.6111
Narrabri | 880/2 | 66 | Burren Junction ZS | Walgett ZS | 13 | 0 | 0 | 0 | 0 | 0
Narrabri | 890:BRE | 66 | Walgett ZS | Brewarrina ZS | 15 | 0.408 | 0.431 | 0.453 | 0.474 | 0.494
Narrabri | 895:LGR | 66 | Walgett ZS | Lightning Ridge ZS | 15 | 1.234 | 1.337 | 1.432 | 1.521 | 1.605
Nyngan | 9UT | 132 | Nyngan 132/66kV STS | Nyngan Solar Farm | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 9UW | 132 | Nyngan Solar Farm | Scrubby Valley Sw Stn | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 946/2 | 132 | Scrubby Valley Sw Stn | Cobar CSA ZS | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 946/3 | 132 | Scrubby Valley Sw Stn | Cobar Peak ZS | 102 | 0 | 0 | 0 | 0 | 0
Nyngan | 94R | 132 | Cobar CSA ZS | Cobar Elura ZS | 128 | 0 | 0 | 0 | 0 | 0
Nyngan | 811 | 66 | Nyngan 132/66kV STS | Cobar Town ZS | 10 | 3.6218 | 3.7623 | 3.8955 | 4.0223 | 4.1445
Nyngan | 854 | 66 | Nyngan 132/66kV STS | Nyngan Town ZS | 15 | 7.104 | 7.193 | 7.279 | 7.362 | 7.442
Nyngan | 820/1:NYN | 66 | Nyngan Town ZS | Nevertire Tee | 15 | 0 | 0 | 0 | 0 | 0
Nyngan | 820:NVE | 66 | Nyngan 132/66kV STS | Nevertire ZS | 11 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/1 | 66 | Nyngan 132/66kV STS | Girilambone Tee | 28 | 1.1215 | 1.1462 | 1.1709 | 1.1943 | 1.2176
Nyngan | 855/1a | 66 | Girilambone Tee | Girilambone ZS | 24 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/2 | 66 | Girilambone Tee | Byrock Tee | 28 | 1.4019 | 1.4328 | 1.4637 | 1.4929 | 1.5221
Nyngan | 855/3 | 66 | Byrock Tee | Bourke ZS | 28 | 1.0494 | 1.08 | 1.1106 | 1.1394 | 1.1682
Nyngan | 855/3a | 66 | Byrock Tee | Byrock ZS | 15 | 0.02 | 0.021 | 0.022 | 0.023 | 0.024
Nyngan | 855/4 | 66 | Girilambone ZS | Tritton Mine ZS | 24 | 0 | 0 | 0 | 0 | 0
Oberon | 94C | 132 | TransGrid Wallerawang 330/132/66kV STS | Oberon 132 ZS | 128 | 0 | 0 | 0 | 0 | 0
Oberon | 856 | 66 | TransGrid Wallerawang 330/132/66kV STS | Oberon Town ZS | 28 | 2.0704 | 2.1893 | 2.3012 | 2.4081 | 2.51
Oberon | 81B | 33 | Oberon Town ZS | Burraga ZS | 8 | 0 | 0 | 0 | 0 | 0
Orange | 94G | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 0 | 0 | 0 | 0 | 0
Orange | 9MC | 132 | TransGrid Orange North 132kV Sw Stn | Flyers Creek Sw Stn | 142 | 0 | 0 | 0 | 0 | 0
Orange | 9MR | 132 | Flyers Creek Sw Stn | Cadia ZS | 180 | 0 | 0 | 0 | 0 | 0
Orange | 807 | 66 | TransGrid Orange 132/66kV STS | Orange West & South Tee | 61 | 7.069 | 7.564 | 8.03 | 8.469 | 8.887
Orange | 807/2 | 66 | Orange West & South Tee | Orange South ZS | 63 | 0 | 0 | 0 | 0 | 0
Orange | 807/3 | 66 | Orange West & South Tee | Orange West ZS | 62 | 7.069 | 7.564 | 8.03 | 8.469 | 8.887
Orange | 818/1 | 66 | TransGrid Orange 132/66kV STS | Blayney ZS | 11 | 0 | 0 | 0 | 0 | 0
Orange | 8C2 | 66 | TransGrid Orange 132/66kV STS | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0
Orange | 8F1 | 66 | TransGrid Orange 132/66kV STS | Orange South ZS | 63 | 8.3811 | 9.0436 | 9.661 | 10.2407 | 10.7898
Orange | 8M1 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 11 | 7.188 | 7.647 | 8.081 | 8.492 | 8.885
Orange | 8M2 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 21 | 0 | 0 | 0 | 0 | 0
Parkes | 300 | 132 | TransGrid Parkes 132/66kV STS | North Parkes Mine ZS | 87 | 0 | 0 | 0 | 0 | 0
Parkes | 898 | 66 | TransGrid Parkes 132/66kV STS | Trundle ZS | 10 | 6.7882 | 6.7882 | 6.7882 | 6.7882 | 6.7882
Parkes | 899 | 66 | Parkes Town ZS | Peak Hill ZS | 12 | 4.6568 | 4.6976 | 4.736 | 4.772 | 4.8072
Parkes | 89G | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 61 | 6.068 | 6.266 | 6.454 | 6.6335 | 6.8055
Parkes | 89L | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 39 | 5.4612 | 5.6394 | 5.8086 | 5.9702 | 6.125
Parkes | 89M | 66 | Peak Hill ZS | Tomingley Mine ZS | 32 | 0 | 0 | 0 | 0 | 0
Tamworth | 801 | 66 | Transgrid Tamworth 132/66kV STS | Oxley Vale ZS | 63 | 5.4623 | 5.8425 | 6.2002 | 6.5385 | 6.8602
Tamworth | 803 | 66 | Transgrid Tamworth 132/66kV STS | South Tamworth ZS | 70 | 9.9238 | 10.5835 | 11.2058 | 11.7945 | 12.3558
Tamworth | 804 | 66 | Transgrid Tamworth 132/66kV STS | Nundle ZS | 8 | 0.524 | 0.542 | 0.56 | 0.577 | 0.593
Tamworth | 806 | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 38 | 3.3207 | 3.5198 | 3.7086 | 3.8879 | 4.0583
Tamworth | 873 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 3.4187 | 3.6392 | 3.8475 | 4.045 | 4.2336
Tamworth | 874 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 3.5583 | 3.7878 | 4.0045 | 4.21 | 4.4064
Tamworth | 803/2 | 66 | South Tamworth ZS | Oxley Vale ZS | 63 | 1.8208 | 1.9475 | 2.0667 | 2.1795 | 2.2868
Tamworth | 806/1 | 66 | Goddard Lane ZS | Attunga ZS | 18 | 3.1604 | 3.3262 | 3.4843 | 3.6356 | 3.7792
Tamworth | 806/2 | 66 | Attunga ZS | Manilla ZS | 18 | 2.2834 | 2.4102 | 2.5313 | 2.6466 | 2.7562
Tamworth | 806/3 | 66 | Manilla ZS | Upper Manilla ZS | 18 | 0.8694 | 0.9162 | 0.9603 | 1.0026 | 1.0422
Tamworth | 806/4 | 66 | Upper Manilla ZS | Barraba ZS | 15 | 0.921 | 0.971 | 1.018 | 1.063 | 1.106
Tamworth | 80C | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 61 | 2.9447 | 3.1214 | 3.2887 | 3.4477 | 3.5989
Tamworth | 813:CLA | 66 | Transgrid Tamworth 132/66kV STS | Currububula ZS | 28 | 7.3659 | 7.7561 | 8.1259 | 8.4792 | 8.8179
Tamworth | 813/1:QDI | 66 | Currububula ZS | Werris Creek ZS | 28 | 7.0849 | 7.4671 | 7.8289 | 8.1752 | 8.5069
Tamworth | 813/2:QDI | 66 | Werris Creek ZS | Quirindi ZS | 28 | 1.807 | 1.902 | 1.991 | 2.077 | 2.159
Tamworth | 870/1:KTL | 66 | Transgrid Tamworth 132/66kV STS | Kootingal Tee | 14 | 2.663 | 2.817 | 2.961 | 3.098 | 3.231
Tamworth | 870/2:KTL | 66 | Kootingal Tee | Kootingal ZS | 12 | 2.372 | 2.511 | 2.642 | 2.766 | 2.886
Tamworth | 870/3:KTL | 66 | Kootingal Tee | Bendemeer ZS | 13 | 0.291 | 0.306 | 0.319 | 0.332 | 0.345
Tamworth | 798 | 33 | Quirindi ZS | Murrurundi ZS | 4 | 1.01 | 1.07 | 1.126 | 1.18 | 1.231
Tamworth | 799/1 | 33 | Quirindi ZS | Caroona Tee | 6 | 0.49519 | 0.50251 | 0.5117 | 0.51908 | 0.52647
Tamworth | 799/2 | 33 | Caroona Tee | Caroona ZS | 4 | 0.047 | 0.048 | 0.05 | 0.052 | 0.053
Tamworth | 799/3 | 33 | Caroona Tee | Spring Ridge ZS | 3 | 0.065 | 0.067 | 0.069 | 0.07 | 0.072
Tamworth | 799/4 | 33 | Spring Ridge ZS | Colly Blue ZS | 3 | 0.141 | 0.146 | 0.152 | 0.157 | 0.162
Wellington | 945/3 | 132 | TransGrid Line 945 Wellington 132kV Tee | Wellington 132kV ZS | 124 | 2.553 | 2.741 | 2.917 | 3.083 | 3.241
Wellington | 947/1 | 132 | TransGrid Line 947 Burrendong Tee | Burrendong Hydro | 36 | 0 | 0 | 0 | 0 | 0
Wellington | 94F | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 43.5332 | 44.9054 | 46.2081 | 47.4501 | 48.6391
Wellington | 94J | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 40.3458 | 41.6176 | 42.8249 | 43.9759 | 45.0779
Wellington | 805 | 66 | Wellington 132kV ZS | Mumbil ZS | 11 | 0.358 | 0.388 | 0.415 | 0.441 | 0.465
Wellington | 813:WGN | 66 | Wellington 132kV ZS | Geurie Tee | 12 | 0 | 0 | 0 | 0 | 0
Albury | 997/1 | 132 | Union Rd ZS | Corowa ZS | 128 | 33.5504 | 33.828 | 34.0944 | 34.3488 | 34.5928
Albury | 997/2 | 132 | Corowa ZS | Mulwala ZS | 128 | 6.6712 | 6.828 | 6.9768 | 7.1184 | 7.2536
Albury | 99E | 132 | Union Rd ZS | Jelbart ZS | 148 | 3.858 | 4.12 | 4.366 | 4.5995 | 4.821
Albury | 99G | 132 | Union Rd ZS | Jelbart ZS | 148 | 3.858 | 4.12 | 4.366 | 4.5995 | 4.821
Bega | 84G | 66 | Bega 132/66kV STS | Eden South ZS | 61 | 1.9581 | 2.0831 | 2.2001 | 2.3113 | 2.4181
Bega | 84H | 66 | Eden South ZS | Edrom ZS | 38 | 0 | 0 | 0 | 0 | 0
Bega | 84M | 66 | Bega 132/66kV STS | Maher St ZS | 61 | 2.7788 | 2.9327 | 3.0782 | 3.2162 | 3.3483
Bega | 89A | 66 | Bega 132/66 | Pambula ZS | 38 | 5.2461 | 5.6178 | 5.9661 | 6.2946 | 6.6078
Bega | 84P | 66 | Bega 132/66kV STS | Maher St ZS | 38 | 2.7788 | 2.9327 | 3.0782 | 3.2162 | 3.3483
Bega | 89F | 66 | Pambula ZS | Eden South ZS | 30 | 0.64176 | 0.68082 | 0.71736 | 0.75222 | 0.78582
Bega | 84R/1 | 66 | Maher St ZS | Quira ZS | 6 | 0 | 0 | 0 | 0 | 0
Bega | 7802/1 | 33 | Maher St ZS | Brogo ZS | 12 | 0 | 0 | 0 | 0 | 0
Bega | 7802/2 | 33 | Brogo ZS | Cobargo ZS | 10 | 2.634 | 2.817 | 2.989 | 3.151 | 3.306
Bega | 7814 | 33 | Cobargo ZS | Bermagui ZS | 5 | 1.652 | 1.777 | 1.894 | 2.004 | 2.108
Buronga | 87G | 66 | Dareton ZS | Ellerslie ZS | 67 | 0.342 | 0.351 | 0.36 | 0.3681 | 0.3762
Buronga | 87H/1 | 66 | Ellerslie ZS | Ginkgo Snapper Tee | 45 | 0 | 0 | 0 | 0 | 0
Buronga | 87H/2 | 66 | Ginkgo Snapper Tee | Ginkgo ZS | 20 | 0 | 0 | 0 | 0 | 0
Buronga | 87H/3 | 66 | Ginkgo Snapper Tee | Snapper ZS | 12 | 0 | 0 | 0 | 0 | 0
Buronga | 83U | 66 | Powercor Mildura ZS (NSW Border) | Buronga ZS | 22 | 7.922 | 8.284 | 8.625 | 8.948 | 9.256
Buronga | 83W | 66 | Buronga ZS | Dareton ZS | 22 | 0 | 0 | 0 | 0 | 0
Buronga | Merbein - Dareton Line | 66 | Powercor Mildura ZS (NSW Border) | Dareton ZS | 49 | 0.38304 | 0.39312 | 0.4032 | 0.41227 | 0.42134
Coleambally | CLY1526/1 | 33 | Coleambally 132/33kV STS | Coleambally Tee | 10 | 0.3905 | 0.4037 | 0.4147 | 0.4268 | 0.4378
Coleambally | CLY1526/2 | 33 | Coleambally Tee | Coleambally ZS | 10 | 0.355 | 0.367 | 0.377 | 0.388 | 0.398
Coleambally | CLY1526/3 | 33 | Coleambally Tee | Egansford ZS | 8 | 0.0847 | 0.0891 | 0.0946 | 0.099 | 0.1034
Coleambally | CLY1530/1 | 33 | Coleambally 132/33kV STS | Ringwood Rd ZS | 8 | 0.97428 | 1.0083 | 1.0405 | 1.0718 | 1.1022
Coleambally | CLY1530/2 | 33 | Ringwood Rd ZS | Darlington Point ZS | 8 | 0.734 | 0.764 | 0.792 | 0.819 | 0.846
Cooma | 974 | 132 | TransGrid Cooma 132/66kV STS | Bega 132/66kV STS | 128 | 7.4067 | 7.9033 | 8.3707 | 8.8134 | 9.2346
Cooma | 97R/1 | 132 | TransGrid Cooma 132/66kV STS | Steeple Flat 132/66kV STS | 140 | 21.8428 | 22.4061 | 22.9395 | 23.4475 | 23.9331
Cooma | 82D | 66 | TransGrid Cooma 132/66kV STS | Jindabyne East ZS | 20 | 3.4233 | 3.632 | 3.8277 | 4.011 | 4.1853
Cooma | 84J | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 70 | 1.831 | 1.9245 | 2.013 | 2.0985 | 2.18
Cooma | 84L | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 64 | 1.831 | 1.9245 | 2.013 | 2.0985 | 2.18
Cooma | 82J/1 | 66 | Snowy Adit 132/66/11kV ZS | Snowy Lookout Sw Stn | 12 | 0 | 0 | 0 | 0 | 0
Cooma | 82J/2 | 66 | Jindabyne ZS | Snowy Lookout Sw Stn | 12 | 0.14142 | 0.14142 | 0.14142 | 0.14142 | 0.14142
Cooma | 82R | 66 | Jindabyne East ZS | Jindabyne ZS | 20 | 1.5435 | 1.6245 | 1.7005 | 1.772 | 1.8395
Cooma | 888/1 | 66 | TransGrid Cooma 132/66kV STS | Rhine Falls Sw Stn | 16 | 0.82265 | 0.84598 | 0.8694 | 0.89102 | 0.91271
Cooma | 888/3 | 66 | Rhine Falls Sw Stn | Adaminaby ZS | 16 | 0.53739 | 0.56098 | 0.58363 | 0.60532 | 0.62703
Cooma | 888/4 | 66 | Rhine Falls Sw Stn | Eucumbene Tee | 15 | 0.17042 | 0.17123 | 0.17286 | 0.17368 | 0.1745
Cooma | 888/6 | 66 | Eucumbene Tee | Eucumbene ZS | 15 | 0.038 | 0.039 | 0.041 | 0.042 | 0.043
Cooma | 888/7 | 66 | Eucumbene Tee | Snowy Adit 132/66/11kV ZS | 20 | 0 | 0 | 0 | 0 | 0
Cooma | 849/1 | 33 | Adaminaby ZS | Providence Portal ZS | 7 | 0 | 0 | 0 | 0 | 0
Cowra | 865 | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 4.22 | 4.5005 | 4.7645 | 5.0145 | 5.2525
Cowra | 863:CWD | 66 | TransGrid Cowra 132/66kV STS | Canowindra ZS | 9 | 1.999 | 2.141 | 2.275 | 2.401 | 2.521
Cowra | 866:COW | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 4.22 | 4.5005 | 4.7645 | 5.0145 | 5.2525
Cowra | 891/1 | 66 | TransGrid Cowra 132/66kV STS | Wyangala Dam Tee | 20 | 31.4518 | 31.4376 | 31.4236 | 31.4107 | 31.3975
Cowra | 891/2 | 66 | Wyangala Dam Tee | Wyangala Dam | 19 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 31.8198
Cowra | 891/5 | 66 | Monteagle Tee | Monteagle ZS | 13 | 0.261 | 0.269 | 0.277 | 0.284 | 0.292
Cowra | 891/6 | 66 | Monteagle Tee | Young ZS | 19 | 0 | 0 | 0 | 0 | 0
Cowra | 891/7 | 66 | Bendick Murrell Tee | Bendick Murrell ZS | 19 | 0.841 | 0.876 | 0.91 | 0.942 | 0.974
Cowra | 891:BMU/1 | 66 | Wyangala Dam Tee | Bendick Murrell Tee | 19 | 1.0469 | 1.0877 | 1.1277 | 1.1647 | 1.2027
Cowra | 891:BMU/2 | 66 | Bendick Murrell Tee | Monteagle Tee | 19 | 0.261 | 0.269 | 0.277 | 0.284 | 0.292
Cowra | 893/1 | 66 | TransGrid Cowra 132/66kV STS | Grenfell Tee | 12 | 2.112 | 2.251 | 2.381 | 2.504 | 2.622
Cowra | 893/4 | 66 | Grenfell Tee | Payten's Bridge ZS | 12 | 0 | 0 | 0 | 0 | 0
Cowra | 893/6 | 66 | Grenfell Tee | Grenfell ZS | 12 | 2.112 | 2.251 | 2.381 | 2.504 | 2.622
Darlington Point | 99N | 132 | TransGrid Darlington Point 330/132kV STS | Hillston ZS | 128 | 3.0595 | 3.2004 | 3.3356 | 3.4655 | 3.5908
Darlington Point | 99R | 132 | TransGrid Darlington Point 330/132kV STS | Hay 132 ZS | 128 | 2.1925 | 2.1992 | 2.2059 | 2.2127 | 2.2194
Darlington Point | HAT 22 | 33 | Hay 132 ZS | Hay ZS | 8 | 1.5764 | 1.6586 | 1.7377 | 1.8127 | 1.8846
Darlington Point | HAT 32 | 33 | Hay 132 ZS | Hay ZS | 8 | 0.3941 | 0.41466 | 0.43442 | 0.45318 | 0.47114
Darlington Point | HAT 42 | 33 | Hay 132 ZS | Carrathool ZS | 7 | 0.5515 | 0.5621 | 0.5727 | 0.5823 | 0.5919
Darlington Point | HIL1117 | 33 | Hillston ZS | Ivanhoe ZS | 8 | 1.1906 | 1.2564 | 1.3188 | 1.3778 | 1.4352
Deniliquin | 844 | 66 | TransGrid Deniliquin 132/66kV STS | Barham ZS | 11 | 1.5653 | 1.6444 | 1.72 | 1.7923 | 1.8618
Deniliquin | 845 | 66 | TransGrid Deniliquin 132/66kV STS | Deniliquin ZS | 38 | 5.9537 | 6.2545 | 6.5419 | 6.817 | 7.0813
Deniliquin | 822/1 | 66 | TransGrid Deniliquin 132/66kV STS | Murgha ZS | 11 | 2.047 | 2.1504 | 2.2493 | 2.3438 | 2.4347
Deniliquin | 822/2 | 66 | Murgha ZS | Moulamein ZS | 11 | 1.7125 | 1.799 | 1.8817 | 1.9608 | 2.0369
Deniliquin | 84Y | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 66 | 2.3012 | 2.4175 | 2.5286 | 2.6349 | 2.737
Deniliquin | MM61 | 66 | Moulamein ZS | Koraleigh ZS | 15 | 1.1372 | 1.1947 | 1.2496 | 1.3021 | 1.3526
Deniliquin | No.6 Moama | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 34 | 1.6055 | 1.6866 | 1.7641 | 1.8383 | 1.9096
Finley | 9R4 | 132 | TransGrid Finley 132/66kV STS | Mulwala ZS | 140 | 0 | 0 | 0 | 0 | 0
Finley | 84A | 66 | TransGrid Finley 132/66kV STS | Jerilderie ZS | 15 | 0.939 | 0.973 | 1.005 | 1.037 | 1.068
Finley | 84B | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 2.0104 | 2.0713 | 2.1294 | 2.1858 | 2.2403
Finley | 84C | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 3.7336 | 3.8467 | 3.9546 | 4.0592 | 4.1607
Goulburn | 972 | 132 | TransGrid Marulan 330/132kV STS | Goulburn 132/66/33kV STS | 180 | 21.7773 | 22.8213 | 23.8032 | 24.7338 | 25.6194
Goulburn | 9UR | 132 | TransGrid Marulan 330/132kV STS | Taralga Wind Farm | 140 | 0 | 0 | 0 | 0 | 0
Goulburn | 843 | 66 | Clinton St ZS | Goulburn North ZS | 46 | 1.6024 | 1.7211 | 1.8316 | 1.9363 | 2.0352
Goulburn | 82K/2 | 66 | Woodlawn ZS | Bungendore ZS | 28 | 0 | 0 | 0 | 0 | 0
Goulburn | 840:GOU | 66 | Goulburn 132/66/33kV STS | Goulburn North ZS | 61 | 4.6407 | 4.9248 | 5.1927 | 5.4463 | 5.6895
Goulburn | 841:GBN | 66 | Goulburn North ZS | Crookwell ZS | 9 | 1.946 | 2.042 | 2.135 | 2.223 | 2.308
Goulburn | 850:GOU | 66 | Goulburn 132/66/33kV STS | Woodlawn ZS | 28 | 7.893 | 7.946 | 7.996 | 8.043 | 8.087
Goulburn | 86M/1 | 66 | Goulburn 132/66/33kV STS | Marulan North Tee | 25 | 1.4769 | 1.5921 | 1.6992 | 1.7991 | 1.8945
Goulburn | 86M/2 | 66 | Marulan North Tee | Marulan South ZS | 25 | 0 | 0 | 0 | 0 | 0
Goulburn | 86L | 66 | Marulan North Tee | Marulan North ZS | 12 | 1.641 | 1.769 | 1.888 | 1.999 | 2.105
Goulburn | 870:GOU | 66 | Goulburn 132/66/33kV STS | Clinton St ZS | 34 | 8.7968 | 9.3855 | 9.9372 | 10.4598 | 10.9574
Goulburn | GOU12 | 33 | Goulburn 132/66/33kV STS | Brisbane Grove ZS | 7 | 1.238 | 1.315 | 1.387 | 1.456 | 1.522
Griffith | 79C/1 | 33 | TransGrid Griffith 132/33kV STS | Widgelli / Willbriggie Tee | 10 | 1.1669 | 1.2246 | 1.2798 | 1.3326 | 1.3835
Griffith | 79C/2 | 33 | Widgelli / Willbriggie Tee | Widgelli ZS | 10 | 0.22641 | 0.23761 | 0.24831 | 0.25857 | 0.26844
Griffith | 79C/3 | 33 | Widgelli / Willbriggie Tee | Willbriggie Tee | 10 | 0.94046 | 0.98701 | 1.0315 | 1.0741 | 1.115
Griffith | 79C/4 | 33 | Willbriggie Tee | Willbriggie ZS | 10 | 0.83597 | 0.87734 | 0.91685 | 0.95472 | 0.99115
Griffith | 79C/5 | 33 | Willbriggie Tee | 79C / 79P Tee | 10 | 0.1045 | 0.10967 | 0.11461 | 0.11934 | 0.12389
Griffith | 79F | 33 | TransGrid Griffith 132/33kV STS | Yenda ZS | 22 | 2.2815 | 2.3944 | 2.5022 | 2.6056 | 2.705
Griffith | 79G | 33 | Beelbangera ZS | Griffith ZS | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79J | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 0 | 0 | 0 | 0 | 0
Griffith | 79L | 33 | TransGrid Griffith 132/33kV STS | Beelbangera ZS | 10 | 2.5427 | 2.6686 | 2.7887 | 2.9039 | 3.0148
Griffith | 79M | 33 | TransGrid Griffith 132/33kV STS | Hanwood ZS | 22 | 0.855 | 0.873 | 0.891 | 0.909 | 0.926
Griffith | 79P | 33 | TransGrid Griffith 132/33kV STS | Warrawidgee Tee | 22 | 1.7938 | 1.8826 | 1.9674 | 2.0487 | 2.1268
Griffith | 79W/1 | 33 | Warrawidgee Tee | Warrawidgee ZS | 6 | 0.41798 | 0.43867 | 0.45842 | 0.47736 | 0.49558
Griffith | 79W/2 | 33 | Warrawidgee Tee | Nericon Tee | 21 | 1.254 | 1.316 | 1.3753 | 1.4321 | 1.4867
Griffith | 79W/3 | 33 | Nericon Tee | Nericon ZS | 20 | 0.55731 | 0.5849 | 0.61123 | 0.63648 | 0.66077
Griffith | 79R | 33 | TransGrid Griffith 132/33kV STS | Tharbogang ZS | 31 | 4.628 | 4.864 | 5.089 | 5.304 | 5.511
Griffith | 79U | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 6.069 | 6.352 | 6.623 | 6.883 | 7.134
Harden - Murrumburrah | 836 | 66 | TransGrid Murrumburrah 132/66kV STS | Cootamundra ZS | 20 | 8.414 | 8.7 | 8.97 | 9.224 | 9.466
Harden - Murrumburrah | 837 | 66 | TransGrid Murrumburrah 132/66kV STS | Jugiong ZS | 12 | 0.178 | 0.185 | 0.192 | 0.199 | 0.205
Harden - Murrumburrah | 847 | 66 | TransGrid Murrumburrah 132/66kV STS | Boorowa ZS | 10 | 3.8451 | 3.8922 | 3.9369 | 3.9809 | 4.0224
Harden - Murrumburrah | 823/3 | 66 | Bogalara Sw Stn | Marilba ZS | 12 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 830/1:PCR | 66 | Bogalara Sw Stn | Parsons Creek ZS | 11 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 838/3 | 66 | Jugiong ZS | Bogalara Sw Stn | 12 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 83A | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 1.784 | 1.894 | 1.998 | 2.097 | 2.192
Harden - Murrumburrah | 83D | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 890:YOU | 66 | TransGrid Murrumburrah 132/66kV STS | Young ZS | 24 | 5.168 | 5.455 | 5.728 | 5.988 | 6.238
Moruya North | 98H | 132 | Endeavour Energy Evans Lane Sw Stn | Moruya North 132/33kV STS | 180 | 11.0427 | 11.843 | 12.5928 | 13.3 | 13.9714
Moruya North | 98M | 132 | Endeavour Energy Evans Lane Sw Stn | Batemans Bay ZS | 50 | 9.7686 | 10.4765 | 11.1398 | 11.7654 | 12.3593
Moruya North | 98T | 132 | Batemans Bay ZS | Moruya North 132/33kV STS | 61 | 2.1236 | 2.2775 | 2.4217 | 2.5577 | 2.6868
Moruya North | 7703 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 30 | 3.7509 | 4.0166 | 4.266 | 4.5017 | 4.7253
Moruya North | 7704 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 26 | 4.7976 | 5.1376 | 5.4566 | 5.758 | 6.0439
Moruya North | 7706 | 33 | Moruya North 132/33kV STS | Mossy Point ZS | 25 | 5.0043 | 5.3949 | 5.7592 | 6.1005 | 6.4249
Moruya North | 7712 | 33 | Bodalla Tee | Bodalla ZS | 10 | 0.735 | 0.78015 | 0.82215 | 0.86205 | 0.9009
Moruya North | 7713 | 33 | Bodalla Tee | Narooma ZS | 21 | 0 | 0 | 0 | 0 | 0
Moruya North | 7817 | 33 | Narooma Tee | Cobargo ZS | 10 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/1 | 33 | Moruya Town ZS | Tuross Tee | 17 | 2.2353 | 2.3969 | 2.5479 | 2.6904 | 2.8262
Moruya North | 7711/2 | 33 | Tuross Tee | Tuross ZS | 7 | 1.7356 | 1.869 | 1.9939 | 2.1115 | 2.2229
Moruya North | 7711/3 | 33 | Tuross Tee | Bodalla Tee | 21 | 0.756 | 0.80244 | 0.84564 | 0.88668 | 0.92664
Moruya North | 7715/1 | 33 | Moruya Town ZS | Narooma Tee | 30 | 3.4771 | 3.7279 | 3.9633 | 4.1855 | 4.3956
Moruya North | 7715/2 | 33 | Narooma Tee | Narooma ZS | 10 | 3.319 | 3.5585 | 3.7832 | 3.9952 | 4.1958
Morven | 996/1 | 132 | TransGrid 132kV Line 996 Tee | Morven 132/66kV STS | 45 | 2.84 | 2.95 | 3.056 | 3.158 | 3.257
Morven | 83M/3 | 66 | Morven 132/66kV STS | Culcairn ZS | 15 | 1.627 | 1.685 | 1.742 | 1.797 | 1.85
Morven | 83M/4 | 66 | Morven 132/66kV STS | Holbrook ZS | 15 | 1.247 | 1.3 | 1.351 | 1.401 | 1.449
Munyang | 56 | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.1576 | 0.1688 | 0.1792 | 0.1888 | 0.1984
Munyang | 57A | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.0636 | 0.0702 | 0.0756 | 0.0816 | 0.0864
Munyang | 57B | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.0424 | 0.0468 | 0.0504 | 0.0544 | 0.0576
Munyang | No.1 Perisher | 33 | TransGrid Munyang 132/33kV STS | Smiggin Sw Stn | 38 | 0.1576 | 0.1688 | 0.1792 | 0.1888 | 0.1984
Munyang | No.2 Perisher/1 | 33 | TransGrid Munyang 132/33kV STS | Blue Cow Tee | 38 | 0.114 | 0.125 | 0.134 | 0.144 | 0.152
Munyang | No.2 Perisher/2 | 33 | Blue Cow Tee | Smiggin Sw Stn | 38 | 0.106 | 0.117 | 0.126 | 0.136 | 0.144
Munyang | 60/2 | 33 | Bullocks Portal ZS | Bullocks Flat ZS | 19 | 0.1379 | 0.1477 | 0.1568 | 0.1652 | 0.1736
Munyang | 58 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.70711 | 0.70711 | 0.70711 | 0.70711 | 0.70711
Munyang | 59 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.0238 | 0.0238 | 0.0238 | 0.0238 | 0.0238
Munyang | Bullocks Portal Line | 33 | Perisher ZS | Bullocks Portal ZS | 20 | 0.1576 | 0.1688 | 0.1792 | 0.1888 | 0.1984
Queanbeyan | 97Y | 132 | TransGrid Williamsdale 330/132kV STS | Googong Town ZS | 91 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 975 | 132 | TransGrid Queanbeyan 132/66kV STS | Googong Town ZS | 41 | 8.728 | 9.445 | 10.111 | 10.735 | 11.326
Queanbeyan | 82A | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 6.669 | 7.1694 | 7.6368 | 8.0778 | 8.4954
Queanbeyan | 82B | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 5.0018 | 5.377 | 5.7276 | 6.0583 | 6.3716
Queanbeyan | 82F | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 49 | 5.281 | 5.665 | 6.024 | 6.363 | 6.685
Queanbeyan | 82G | 66 | TransGrid Queanbeyan 132/66kV STS | Captains Flat ZS | 12 | 2.2481 | 2.373 | 2.4911 | 2.6033 | 2.7097
Queanbeyan | 82K | 66 | TransGrid Queanbeyan 132/66kV STS | Sutton / Bungendore Tee | 28 | 7.7743 | 8.2207 | 8.6433 | 9.0439 | 9.4265
Queanbeyan | 82K/1 | 66 | Sutton / Bungendore Tee | Bungendore ZS | 28 | 5.4103 | 5.7299 | 6.0315 | 6.3171 | 6.5888
Queanbeyan | 82K/3 | 66 | Sutton / Bungendore Tee | Sutton ZS | 28 | 2.3641 | 2.491 | 2.6119 | 2.7268 | 2.8378
Queanbeyan | 82M | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 20 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 830:QSH | 66 | Queanbeyan South ZS | Googong Dam ZS | 15 | 0.73859 | 0.73859 | 0.73859 | 0.73859 | 0.73859
Steeple Flat | 97C | 132 | Steeple Flat 132/66kV STS | Boco Rock Wind Farm | 140 | 0 | 0 | 0 | 0 | 0
Steeple Flat | 97R/2 | 132 | Steeple Flat 132/66kV STS | Bega 132/66kV STS | 140 | 7.6047 | 8.1145 | 8.5944 | 9.049 | 9.4814
Steeple Flat | 84R/5 | 66 | Steeple Flat 132/66kV STS | Brown Mountain Hydro | 70 | 0 | 0 | 0 | 0 | 0
Steeple Flat | 810/4 | 66 | Steeple Flat 132/66kV STS | Bombala ZS | 21 | 0.782 | 0.837 | 0.888 | 0.937 | 0.983
Steeple Flat | 84R/3 | 66 | Brown Mountain Hydro | Quira ZS | 70 | 0.585 | 0.631 | 0.674 | 0.714 | 0.752
Temora | 901 | 132 | Temora 132/66 STS | Wyalong Switching Station | 108 | 0 | 0 | 0 | 0 | 0
Temora | 9JW | 132 | Wyalong Switching Station | West Wyalong Switching Station | 108 | 0 | 0 | 0 | 0 | 0
Temora | 9JX | 132 | West Wyalong Switching Station | Lake Cowal | 108 | 0 | 0 | 0 | 0 | 0
Temora | 4 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 0 | 0 | 0 | 0 | 0
Temora | 5 | 66 | Temora 132/66 STS | Ariah Park Tee | 21 | 3.7778 | 3.9816 | 4.1756 | 4.361 | 4.5389
Temora | 6 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 3.109 | 3.298 | 3.477 | 3.647 | 3.809
Temora | 20-60 | 66 | Ariah Park Tee | West Wyalong ZS | 21 | 3.1482 | 3.318 | 3.4797 | 3.6342 | 3.7824
Temora | 60-70 | 66 | West Wyalong ZS | Anona ZS | 7 | 0.444 | 0.465 | 0.485 | 0.504 | 0.523
Temora | 80-140/1 | 66 | Ariah Park Tee | Ariah Park ZS | 15 | 0.62964 | 0.6636 | 0.69594 | 0.72684 | 0.75648
Temora | 80-140/2 | 66 | Ariah Park Tee | Ardlethan ZS | 11 | 0.291 | 0.308 | 0.323 | 0.338 | 0.353
Temora | 835/J | 66 | Junee Reefs ZS | Junee ZS | 12 | 0 | 0 | 0 | 0 | 0
Temora | 835/T | 66 | Temora 132/66 STS | Junee Reefs ZS | 12 | 0.132 | 0.133 | 0.134 | 0.135 | 0.135
Tumut | 827 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 3.65 | 3.859 | 4.057 | 4.247 | 4.428
Tumut | 828 | 66 | TransGrid Tumut 132/66kV STS | Gundagai South ZS | 11 | 2.043 | 2.147 | 2.245 | 2.339 | 2.429
Tumut | 829 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 0 | 0 | 0 | 0 | 0
Tumut | 831 | 66 | Gundagai South ZS | Nangus ZS | 11 | 0.46098 | 0.48639 | 0.5099 | 0.53247 | 0.55311
Tumut | 848 | 66 | Adelong Tee | Adelong ZS | 12 | 0.689 | 0.721 | 0.752 | 0.781 | 0.809
Tumut | 830/2:GUN | 66 | Gundagai South ZS | Parsons Creek ZS | 11 | 0.1656 | 0.1656 | 0.1656 | 0.1656 | 0.1656
Tumut | 848/1 | 66 | Adelong Tee | Batlow ZS | 21 | 2.2125 | 2.3133 | 2.4101 | 2.5032 | 2.5926
Tumut | 848/2 | 66 | Batlow ZS | Tumbarumba ZS | 22 | 1.644 | 1.712 | 1.778 | 1.842 | 1.903
Tumut | 848/3 | 66 | TransGrid Tumut 132/66kV STS | Adelong Tee | 21 | 2.7637 | 2.8901 | 3.0118 | 3.128 | 3.2397
Tumut | 850:TAL | 66 | TransGrid Tumut 132/66kV STS | Talbingo ZS | 18 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 19.6576
Wagga (Copland St) | 83L | 66 | Hammond Ave ZS | Bomen ZS | 54 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Uranquinty ZS | 28 | 2.432 | 2.552 | 2.668 | 2.777 | 2.883
Wagga (Copland St) | 840/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bulgary ZS | 15 | 0.979 | 1.018 | 1.054 | 1.09 | 1.124
Wagga (Copland St) | 840/2 | 66 | Bulgary ZS | Lockhart ZS | 15 | 0.979 | 1.018 | 1.054 | 1.09 | 1.124
Wagga (Copland St) | 840/3 | 66 | Lockhart Tee | Kywong ZS | 16 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M/1 | 66 | Uranquinty ZS | Henty ZS | 15 | 0.83 | 0.863 | 0.895 | 0.925 | 0.955
Wagga (Copland St) | 83M/2 | 66 | Henty ZS | Culcairn ZS | 15 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8W9 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Ashmont ZS | 34 | 6.246 | 6.7392 | 7.1982 | 7.6284 | 8.0361
Wagga (Copland St) | 8WF/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bourkelands Tee | 34 | 5.862 | 6.308 | 6.724 | 7.115 | 7.487
Wagga (Copland St) | 8WF/2 | 66 | Bourkelands Tee | Kooringal ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WF/3 | 66 | Bourkelands Tee | Bourkelands ZS | 42 | 5.862 | 6.308 | 6.724 | 7.115 | 7.487
Wagga (Copland St) | 8WM | 66 | Hammond Ave ZS | Morrow St ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WO | 66 | Ashmont ZS | Bourkelands ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WP | 66 | Morrow St ZS | Cartwrights Hill ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WR | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 0.97552 | 1.0228 | 1.0686 | 1.1118 | 1.1539
Wagga (Copland St) | 8WT | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 0.91924 | 0.96383 | 1.007 | 1.0476 | 1.0873
Wagga (Copland St) | 8WG | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Kooringal ZS | 34 | 6.625 | 7.101 | 7.547 | 7.969 | 8.369
Wagga North | 99U | 132 | TransGrid Wagga North 132/66kV STS | Sebastopol Sw Stn | 128 | 106.066 | 106.066 | 106.066 | 106.066 | 106.066
Wagga North | 9J6 | 132 | Sebastopol Sw Stn | Temora 132/66 STS | 128 | 4.6174 | 4.8664 | 5.1036 | 5.3302 | 5.5475
Wagga North | 9J5/1 | 132 | TransGrid Wagga North 132/66kV STS | Junee 132/66/11kV ZS | 140 | 5.8766 | 6.1936 | 6.4954 | 6.7838 | 7.0605
Wagga North | 9J5/2 | 132 | Junee 132/66/11kV ZS | Temora 132/66 STS | 140 | 5.247 | 5.53 | 5.7995 | 6.057 | 6.304
Wagga North | 30-90 | 66 | Junee ZS | Coolamon ZS | 6 | 2.259 | 2.375 | 2.4852 | 2.5894 | 2.6888
Wagga North | 834:JUN | 66 | Junee ZS | Bethungra ZS | 11 | 0.53834 | 0.545 | 0.5517 | 0.55758 | 0.5635
Wagga North | 83C/1 | 66 | TransGrid Wagga North 132/66kV STS | Oura ZS | 24 | 0.36304 | 0.37556 | 0.3881 | 0.40068 | 0.41231
Wagga North | 83C/2 | 66 | Oura ZS | Forest Hill ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga North | 83G | 66 | TransGrid Wagga North 132/66kV STS | Bomen ZS | 34 | 3.5586 | 3.7917 | 4.0095 | 4.2147 | 4.4082
Wagga North | 83J | 66 | Bomen ZS | Cartwrights Hill ZS | 34 | 3.5766 | 3.8342 | 4.0749 | 4.3017 | 4.5154
Wagga North | 850:BET | 66 | Bethungra ZS | Cootamundra ZS | 12 | 0 | 0 | 0 | 0 | 0
Wagga North | 7CH/1 | 33 | Cartwrights Hill ZS | Euberta ZS | 4 | 0.47961 | 0.49851 | 0.51643 | 0.53335 | 0.55028
Wagga North | 7CH/2 | 33 | Euberta ZS | Ganmurra ZS | 4 | 0.1926 | 0.20034 | 0.2081 | 0.2149 | 0.22269
Wagga North | Oura-Mates Gully | 33 | Oura ZS | Mates Gully ZS | 3 | 0.57674 | 0.59447 | 0.61124 | 0.629 | 0.64579
Wagga North | Mates Gully-Tarcutta | 33 | Mates Gully ZS | Tarcutta ZS | 4 | 0.308 | 0.32 | 0.331 | 0.343 | 0.354
Wagga North | 8WJ | 66 | TransGrid Wagga North 132/66kV STS | Forest Hill ZS | 11 | 1.7107 | 1.8121 | 1.9065 | 1.996 | 2.0806
Yanco | 840/4 | 66 | Narrandra ZS | Kywong ZS | 16 | 0.098 | 0.105 | 0.112 | 0.118 | 0.124
Yanco | 841:YNC | 66 | TransGrid Yanco 132/33/66kV STS | Narrandera ZS | 15 | 7.0003 | 7.1155 | 7.2269 | 7.3334 | 7.4352
Yanco | 7L3 | 33 | TransGrid Yanco 132/33/66kV STS | Cudgel ZS | 8 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Yanco | 7L6/1 | 33 | TransGrid Yanco 132/33/66kV STS | Whitton / Murrami Tee | 15 | 1.908 | 1.9268 | 1.9457 | 1.9637 | 1.9809
Yanco | 7L6/2 | 33 | Whitton / Murrami Tee | Whitton ZS | 8 | 0.476 | 0.496 | 0.515 | 0.534 | 0.552
Yanco | 7L6/3 | 33 | Whitton / Murrami Tee | Murrami ZS | 6 | 0.149 | 0.151 | 0.154 | 0.156 | 0.158
Yanco | 7L5/1 | 33 | TransGrid Yanco 132/33/66kV STS | Yanco ZS | 8 | 3.2586 | 3.4275 | 3.5892 | 3.7426 | 3.8912
Yanco | 7L5/2 | 33 | Yanco ZS | Leeton ZS | 6 | 2.3866 | 2.5075 | 2.6232 | 2.7336 | 2.8402
Yanco | 7L4 | 33 | TransGrid Yanco 132/33/66kV STS | Leeton ZS | 31 | 2.5854 | 2.7165 | 2.8418 | 2.9614 | 3.0768
Yass | 971(1) | 132 | TransGrid Yass 330/132/66kV STS | Cullerin Range Wind Farm | 106 | 0 | 0 | 0 | 0 | 0
Yass | 971(2) | 132 | Cullerin Range Wind Farm | Gunning Wind Farm | 140 | 0 | 0 | 0 | 0 | 0
Yass | 971(3) | 132 | Cullerin Range Wind Farm | Goulburn 132/66/33kV STS | 106 | 0 | 0 | 0 | 0 | 0
Yass | 976/2 (M) | 132 | TransGrid 132kV Line 976/2(Y) / Murrumbateman Tee | Murrumbateman ZS | 42 | 4.431 | 4.724 | 4.999 | 5.26 | 5.509
Yass | 824 | 66 | TransGrid Yass 330/132/66kV STS | Yass ZS | 12 | 5.73 | 6.043 | 6.341 | 6.625 | 6.898
Yass | 823/5 | 66 | Yass ZS | Marilba ZS | 12 | 0.594 | 0.625 | 0.655 | 0.683 | 0.71

## BSP Export
Connection Point | Forecast PF | Summer Forecast (POE50 MVA)
|  | 24/25 | 25/26 | 26/27 | 27/28 | 28/29
Albury (Corowa) | -0.93041 | 33.599 | 33.75 | 33.897 | 34.038 | 34.174
Albury (Mulwala) | -0.75496 | 8.339 | 8.535 | 8.721 | 8.898 | 9.067
Albury (Union Rd + Jelbart) | 0 | 0 | 0 | 0 | 0 | 0
Armidale | -0.99142 | 19.395 | 20.32 | 21.193 | 22.022 | 22.813
Balranald | 0.709 | 0.553 | 0.56 | 0.567 | 0.574 | 0.581
Beryl | 0.99872 | 6.583 | 6.91 | 7.223 | 7.523 | 7.811
Boambee South | -0.94868 | 10.044 | 10.739 | 11.391 | 12.009 | 12.596
Broken Hill 22kV | -0.95792 | 59.074 | 60.108 | 61.082 | 62.004 | 62.883
Casino | -0.94616 | 10.644 | 11.228 | 11.782 | 12.312 | 12.819
Coffs Harbour | -0.20102 | 31.134 | 33.271 | 35.278 | 37.176 | 38.983
Coleambally | 0.68621 | 6.138 | 6.196 | 6.252 | 6.306 | 6.359
Cooma 132kV | 0.50944 | 16.496 | 17.602 | 18.643 | 19.629 | 20.567
Cooma 66kV | 0.4953 | 4.073 | 4.28 | 4.478 | 4.667 | 4.849
Cowra | -0.3874 | 12.819 | 13.642 | 14.419 | 15.155 | 15.857
Darlington Point | 1 | 5.275 | 5.518 | 5.751 | 5.975 | 6.191
Deniliquin | 0.90913 | 13.379 | 14.055 | 14.701 | 15.319 | 15.913
Dorrigo | 0.325 | 1.923 | 2.024 | 2.119 | 2.211 | 2.299
Dunoon | -0.94009 | 3.466 | 3.664 | 3.852 | 4.031 | 4.202
Evans Lane | 1 | 0 | 0 | 0 | 0 | 0
Finley 132kV | 1 | 0 | 0 | 0 | 0 | 0
Finley 66kV | -0.7009 | 0.942 | 0.978 | 1.014 | 1.048 | 1.081
Forbes | 1 | 8.099 | 8.474 | 8.833 | 9.178 | 9.511
Glen Innes | -0.94514 | 6.007 | 6.317 | 6.613 | 6.895 | 7.167
Griffith | 1 | 17.416 | 18.278 | 19.101 | 19.89 | 20.649
Gunnedah 66kV | 0.98218 | 8.539 | 9.145 | 9.712 | 10.249 | 10.758
Hawks Nest | 1 | 0 | 0 | 0 | 0 | 0
Herons Ck | -0.97262 | 6.943 | 7.347 | 7.729 | 8.094 | 8.442
Inverell | -0.87588 | 11.655 | 12.173 | 12.669 | 13.146 | 13.607
Kempsey 33kV | 0.85823 | 14.893 | 15.91 | 16.867 | 17.772 | 18.633
Koolkhan | -0.6838 | 28.363 | 29.975 | 31.505 | 32.964 | 34.36
Lismore 132kV | -0.8562 | 61.274 | 63.291 | 65.204 | 67.027 | 68.771
Macksville | -0.99823 | 5.938 | 6.347 | 6.731 | 7.095 | 7.441
Manildra | -0.96737 | 0.95 | 0.983 | 1.015 | 1.046 | 1.076
Marulan | 1 | 24.197 | 25.357 | 26.448 | 27.482 | 28.466
Merbein | 1 | 0.38 | 0.39 | 0.4 | 0.409 | 0.418
Mildura | 0.9958 | 7.922 | 8.284 | 8.625 | 8.948 | 9.256
Molong | -0.98052 | 1.898 | 2.002 | 2.101 | 2.196 | 2.286
Moree | -0.97809 | 14.785 | 15.073 | 15.352 | 15.621 | 15.881
Morven | -0.97897 | 2.84 | 2.95 | 3.056 | 3.158 | 3.257
Mudgee | -0.15797 | 8.668 | 9.208 | 9.718 | 10.202 | 10.665
Mullumbimby | 1 | 5.198 | 5.508 | 5.801 | 6.081 | 6.348
Munyang | 0.83915 | 0.261 | 0.289 | 0.315 | 0.338 | 0.36
Murrumbateman | -0.98108 | 4.431 | 4.724 | 4.999 | 5.26 | 5.509
Murrumburrah | 0.61901 | 16.215 | 16.939 | 17.626 | 18.279 | 18.905
Nambucca | -0.78994 | 4.485 | 4.788 | 5.072 | 5.341 | 5.598
Narrabri | 0.31819 | 9.229 | 9.672 | 10.096 | 10.503 | 10.894
Orange 132kV | 1 | 0 | 0 | 0 | 0 | 0
Orange 66kV | -0.84372 | 26.536 | 28.461 | 30.263 | 31.965 | 33.58
Panorama | 0.91288 | 24.967 | 26.792 | 28.501 | 30.113 | 31.643
Parkes 132kV | 1 | 0 | 0 | 0 | 0 | 0
Parkes 66kV | -0.95988 | 18.041 | 18.467 | 18.873 | 19.262 | 19.636
Port Macquarie | 0.068622 | 41.893 | 44.858 | 47.639 | 50.266 | 52.763
Queanbeyan 132kV | -0.87821 | 8.728 | 9.445 | 10.111 | 10.735 | 11.326
Queanbeyan 66kV | -0.31143 | 25.185 | 26.931 | 28.569 | 30.116 | 31.587
Raleigh | -0.88775 | 5.503 | 5.845 | 6.167 | 6.473 | 6.766
Robinvale | 0.97239 | 1.181 | 1.2 | 1.219 | 1.238 | 1.256
Snowy Adit | 1 | 0 | 0 | 0 | 0 | 0
Stroud | -0.55776 | 13.538 | 14.337 | 15.095 | 15.815 | 16.504
Tamworth | 0.99997 | 39.938 | 42.437 | 44.796 | 47.038 | 49.177
Taree 33kV | 0.034937 | 8.729 | 9.284 | 9.808 | 10.305 | 10.779
Taree 66kV | 0.9641 | 25.271 | 27.098 | 28.81 | 30.426 | 31.96
Tenterfield | -0.99118 | 2.342 | 2.462 | 2.576 | 2.685 | 2.789
Terranora | 1 | 55.832 | 58.943 | 61.897 | 64.717 | 67.419
Tumut | 0.33858 | 8.657 | 9.103 | 9.527 | 9.933 | 10.323
Upper Tumut | 0 | 0 | 0 | 0 | 0 | 0
Wagga 66kV | 0.98471 | 23.719 | 25.368 | 26.916 | 28.38 | 29.772
Wagga North 132kV | 1 | 10.494 | 11.06 | 11.599 | 12.114 | 12.608
Wagga North 66kV | 0.99932 | 6.286 | 6.76 | 7.203 | 7.62 | 8.015
Waggamba | 1 | 0 | 0 | 0 | 0 | 0
Wallerawang 132kV | 1 | 0 | 0 | 0 | 0 | 0
Wallerawang 66kV | 0.77567 | 1.968 | 2.087 | 2.199 | 2.306 | 2.408
Wellington 132kV | -0.8921 | 83.879 | 86.523 | 89.033 | 91.426 | 93.717
Yanco | 0.19401 | 18.162 | 18.636 | 19.087 | 19.52 | 19.936
Yass 132kV | 0 | 0 | 0 | 0 | 0 | 0
Yass 66kV | -0.9529 | 6.232 | 6.569 | 6.89 | 7.197 | 7.492

## System Limitations
Feeder - Terranora - BPT3B3 Fingal
Feeder - Terranora - MWN3B2 Norco
Feeder - Terranora - MWN3B8 Uki
Feeder - Lismore - EWE3B1 Brunswick No.1
Feeder - Lismore - WBN3B3 Coraki
Feeder - Grafton - MLN3B4 Townsend
Feeder - Grafton - MLN3B5 Woodford Dale-Leigh
Feeder - Grafton - SGN3B1 Armidale Rd
Feeder - Grafton - SGN3B1 Armidale Rd
Feeder - Grafton - SGN3B4 Ulmarra
Feeder - Port Macquarie - BPM3B3 Oxley
Feeder - Port Macquarie - LKC7781 Cathie Sth
Feeder - Port Macquarie - OPM3B1 Granite St
Feeder - Taree - BNK24787 Old Bar No.2
Feeder - Taree - HGN3B1 Crowdy Head
Feeder - Taree - WTE3B7 Spence St
Feeder - Stroud - BLH3B3 Bulahdelah Nth/Markwell/Newells Ck
Feeder - Hawks Nest - TEA3B4 Tea Gardens
Feeder - Armidale - WLS3B1 Walcha East
Feeder - Armidale - GLS3B2 Rockvale
Feeder - Armidale - GLS3B7 City Central
Feeder - Armidale - HGE3B1 Grafton Rd
Feeder - Inverell - BGA2K13 Horton Valley
Feeder - Inverell - TXS3X06 Yelarbon
Feeder - Moree - MRE8B4 Western Rural
Feeder - Moree - WTR8B2 Poison Gate
Feeder - Narrabri - NBI3B1 M14 Spring Ck
Feeder - Narrabri - NBI8B10 M16 Mount Dowe
Feeder - Narrabri - WWA8B4 M8/M21 Spring Plains Rd
Feeder - Gunnedah - GDH8B15 Sth Gunnedah
Feeder - Tamworth - ATA3B1 Attunga
Feeder - Tamworth - BBA3B4 Barraba
Feeder - Tamworth - ETH3B7 TCC/Calala
Feeder - Tamworth - WCK516 Dewhurst/Gordon
Feeder - Beryl - DNO132 Dunedoo No.1
Feeder - Wellington - WGN72 Yeoval
Feeder - Wellington - WGN72 Yeoval
Feeder - Dubbo - DBS3B8 Margaret Cres
Feeder - Dubbo - DBW3B5 Rural West
Feeder - Dubbo - EUL32 Dubbo Nth/East Town
Feeder - Dubbo - GGB112 Gulargambone
Feeder - Dubbo - GID12 Gilgandra Town No.1
Feeder - Dubbo - GID22 Rural Nth/Sth/West
Feeder - Nyngan - BKE4B2 M82 Wanaaring
Feeder - Broken Hill - BHL42 Railwaytown
Feeder - Broken Hill - MTG4B1 Tibooburra Backbone Line
Feeder - Broken Hill - WLC4B1 White Cliffs
Feeder - Orange - ORS3B2 Jeager Ave
Feeder - Orange - ORS3B3 Email (Electrolux)
Feeder - Orange - ORS3B5 Lords Place
Feeder - Orange - ORS3B7 Anson St Sth
Feeder - Molong - CMK4005 West
Feeder - Bathurst - BNY3B4 Millthorpe
Feeder - Bathurst - BNY3B4 Millthorpe
Feeder - Bathurst - BTH3B6 City Central
Feeder - Bathurst - BTH3B7 Lloyds Rd
Feeder - Bathurst - BTH3B8 Lagoon/Trunkey
Feeder - Bathurst - RAG3B5 OConnell
Feeder - Bathurst - RAG3B6 Limekilns
Feeder - Bathurst - SWT42 Simplot
Feeder - Parkes - PKT3B9 Parkes Town No.3
Feeder - Parkes - TDL8B2 Tullamore/Tottenham
Feeder - Parkes - TDL8B2 Tullamore/Tottenham
Feeder - Forbes - WJL3B3 West Plain
Feeder - Cooma - JYE3B2 Kalkite
Feeder - Steeple Flat - BOM8B2 Nimmitabel
Feeder - Tumut - ADE22 Rural West
Feeder - Tumut - TAL1414 Talbingo Town
Feeder - Yass - YAS6242 Yass Town Sth
Feeder - Wagga (Copland St) - ASM3B9 Ashmont Sth
Feeder - Wagga (Copland St) - HAM3B7 Tarcutta St
Feeder - Wagga (Copland St) - KOO3B1 Plumpton Rd
Feeder - Morven - HOL1890 Wantagong/Woomargama
Feeder - Albury - CRA42 Corurgan
Feeder - Albury - MWA8B4 North St and Rural
Feeder - Finley - FIN8B1 Tocumwal
Feeder - Griffith - BEE1347 Collina No.1
Feeder - Griffith - GFH3B2 Wakaden St
Feeder - Griffith - GFH3B2 Wakaden St
Feeder - Griffith - GFH3B6 Illilliwa
Feeder - Griffith - THA2223 West End

## Comments
A 30MW biomass generator is located at Condong and is connected to the Terranora 110/66kV sub-transmission substation at 66kV via feeders 9504, 9514 and 9502.
A 30MW biomass generator is located at Broadwater and is connected to the Lismore 132/66kV sub-transmission substation at 66kV via feeder 0892.
The Nymboida hydro generation has reached end of life so has been decommissioned.
The 5MW hydro generation at Oaky is presently decommissioned after failure of the dam wall.
A 5MW solar generator is connected to Galloway St zone substation on the 11kV network.
A 2.7MW solar generator is connected to Madgwick Drive zone substation on the 11kV network.
A 5.5MW hydro generator is located at Pindari Dam and is connected to the Transgrid Glen Innes 132/66kV sub-transmission substation at 66kV via feeders 6AE, 6NE, 886 and 887.
A 23MW hydro generator is located at Copeton Dam and is connected to the Transgrid Inverell 132/66kV sub-transmission substation at 66kV via feeders 6BC, 734 and 735.
A 56MW solar generator is located at Moree Solar Farm and is connected to Transgrid’s Moree 132/66kV sub-transmission substation at 66kV via feeder 876.
A 5MW solar generator is located at Wenna on the 22kV network.
A 5MW solar generator is located at Wathagar on the 22kV network.
A 10MW and 6MW gas generator located at Wilga Park is connected to the Transgrid Narrabri 132/66kV sub-transmission substation at 66kV via feeder 861.
A 7MW hydro generator is located at Lake Keepit and is connected to the Transgrid Gunnedah 132/66kV sub-transmission substation at 66kV via feeder 877.
A 1.76MW solar generator is connected to Goddard Lane zone substation on the 11kV network.
A 9.2MW solar generator is located at Narromine on the 22kV network, and a 14.5MW solar generator is connected at Dubbo South on the 11kV network.
A 105MW solar generator is located at Nevertire and is connected to the Dubbo 132/66kV sub-transmission substation at 132kV via the feeder 94W.
A 5MW solar generator is located at Nyngan Town on the 22kV network.
A 4.6MW solar generator is connected to Eulomogo zone substation on the 11kV network.
A 102MW solar generator is located at Nyngan Solar Farm and is connected to the Nyngan 132/66kV sub-transmission substation at 132kV via the feeder 9UT.
A 53MW solar generator is located at Broken Hill and is connected to the Transgrid Broken Hill 220/22kV sub-transmission substation at 22kV.
There have been changes to the water pump network with a new water supply now coming from Wentworth. It is unclear what the long-term configuration will be for the existing water pump infrastructure and whether it will affect peak loads.
A 46.7MW solar generator is located at Manildra on the 11kV network.
A 10MW wind generator is located at Blayney wind farm and is connected to the Transgrid Panorama 132/66kV sub-transmission substation at 66kV via feeders 66:MAN and 81C.
A 1MW solar generator is connected to Stewart zone substation on the 11kV network.
A 4.99MW solar generator is located at Peak Hill on the 11kV network, and a 4.99MW solar generator is located at Trundle on the 22kV network.
A 50MW solar generator is located at West Jemalong and is connected to the Transgrid Forbes 132/66kV sub-transmission substation at 66kV via the feeder 89R.
A 3MW solar thermal generator is located at Lake Cargelligo on the 22kV network, and a 1.1MW solar thermal generator is located at West Jemalong on the 11kV network.
A 5MW hydro generator is located at Brown Mountain Hydro and is connected to Steeple Flat 132/66kV sub-transmission substation at 66kV via feeder 810.
A 114MW wind generator is located at Boco Rock wind farm and is connected to the Steeple Flat 132/66kV sub-transmission substation which is connected to Transgrid’s Cooma 132/66kV sub-transmission substation at 132kV via the feeder 97R.
A 1MW hydro generator is located at Jindabyne Dam and is connected to the Jindabyne zone substation 11kV busbar via feeder JIN22.
Lines 849/2 and 849/3 sustained bushfire damage so are not currently in service. More information is contained in 4.3 Urgent and Unforeseen Investments.
A 15MW hydro generator is located at Jounama Dam and is connected to the Transgrid Tumut 132/66kV sub-transmission substation at 66kV via feeder 850:TAL.
A 7MW biomass generator is located at Woodlawn Bioreactor and is connected to the Woodlawn 66/11kV zone substation at 11kV via feeder WOO8642.
A 5MW wind generator is located at Crookwell wind farm and is connected to the Goulburn 132/66kV sub-transmission substation at 66kV via feeders 841:GBN and 840:GOU.
A 107MW wind generator is located at Taralga wind farm and is connected to the Transgrid Marulan 330/132kV sub-transmission substation at 132kV via feeder 9UR.
A 24MW hydro generator is located at Wyangala Dam and is connected to the Transgrid Cowra 132/66kV sub-transmission substation at 66kV via feeder 891.
A 30MW wind generator is located at Cullerin Range wind farm and is connected to the Transgrid Yass 330/132/66kV sub-transmission substation at 132kV via feeder 971.
A 47MW wind generator is located at Gunning wind farm and is also connected to the Transgrid Yass 330/132/66kV sub-transmission substation at 132kV via feeder 971.
There are multiple load transfer points in the Yass area to other zone substations that can be utilised with the loss of a single Yass transformer.
A 90MW solar generator is located at Sebastopol and is connected to the Transgrid Wagga North 132/66kV sub-transmission substation at 132kV via feeder 99U.
A 90MW solar generator is located at West Wyalong and is connected to the Temora 132/66kV sub-transmission substation at 132kV via feeder 9JW.
A 53MW solar generator is located at Wyalong and is connected to the Temora 132/66kV sub-transmission substation at 132kV via feeder 901.
A 30MW solar generator is located at Junee on the 11kV network.
A 2.2MW generator is connected to Bomen zone substation on the 11kV network.
A 30MW solar thermal generator is located at Corowa on the 22kV network.
A 5MW solar generator is located at Mulwala on the 22kV network.
A 2.5MW hydro generator is located at The Drop and is connected to the Finley 66/22kV zone substation at 22kV via feeder FIN42.
An 85MW solar generator is located at Hillston and is connected to the Hillston 132/66kV sub-transmission substation at 132kV via feeder 9JY.
A 5MW solar generator is located near Egansford and is connected to the Coleambally 132/33kV sub-transmission substation at 33kV via feeder CLY4B4.
A 4.55MW solar generator is connected to Coleambally 132/33kV sub-transmission substation at 33kV.
Two 5MW solar generators are located near Leeton and are connected to the Yanco 132/33kV sub-transmission substation at 33kV via feeder 7L2.
A 4.76MW solar generator is connected to Narrandera zone substation on the 11kV network.
A 1.48MW solar generator is connected to Narrandera zone substation on the 11kV network.
A 3.3MW solar generator is located at Dareton on the 22kV network.