## System Limitations Template
DAPR Limitations Annual Data Essential Energy
asset_name | asset_code | exclude_from_capacity_layers | network | network_element | use_5yr_forecast | voltage_highside | voltage_lowside | investment_description | reliability_criteria | latitude | longitude | latitude_end | longitude_end | res_cust_affected_no | res_cust_affected_percent | primary_driver | augmentation_invest | replacement_invest | connections_invest | other_invest | total_invest | cost_accuracy_plus | cost_accuracy_minus | annual_deferral | deferrable_invest | opex | project_timing | commitment_timing | summer_critical | winter_critical | spring_critical | autumn_critical | summer_nameplate_cap_mva | summer_secure_cap_mva | summer_acc_cap_yr_minus2_mva | summer_acc_cap_yr_minus1_mva | summer_acc_cap_yr0_mva | summer_acc_cap_yr1_mva | summer_acc_cap_yr2_mva | summer_acc_cap_yr3_mva | summer_acc_cap_yr4_mva | summer_acc_cap_yr5_mva | summer_acc_cap_yr6_mva | summer_acc_cap_yr7_mva | summer_acc_cap_yr8_mva | summer_acc_cap_yr9_mva | summer_acc_cap_yr10_mva | summer_load_yr1_poe50_mva | summer_load_yr2_poe50_mva | summer_load_yr3_poe50_mva | summer_load_yr4_poe50_mva | summer_load_yr5_poe50_mva | summer_load_yr6_poe50_mva | summer_load_yr7_poe50_mva | summer_load_yr8_poe50_mva | summer_load_yr9_poe50_mva | summer_load_yr10_poe50_mva | summer_load_yr1_poe10_mva | summer_load_yr2_poe10_mva | summer_load_yr3_poe10_mva | summer_load_yr4_poe10_mva | summer_load_yr5_poe10_mva | summer_load_yr6_poe10_mva | summer_load_yr7_poe10_mva | summer_load_yr8_poe10_mva | summer_load_yr9_poe10_mva | summer_load_yr10_poe10_mva | winter_nameplate_cap_mva | winter_secure_cap_mva | winter_acc_cap_yr_minus2_mva | winter_acc_cap_yr_minus1_mva | winter_acc_cap_yr0_mva | winter_acc_cap_yr1_mva | winter_acc_cap_yr2_mva | winter_acc_cap_yr3_mva | winter_acc_cap_yr4_mva | winter_acc_cap_yr5_mva | winter_acc_cap_yr6_mva | winter_acc_cap_yr7_mva | winter_acc_cap_yr8_mva | winter_acc_cap_yr9_mva | winter_acc_cap_yr10_mva | winter_load_yr1_poe50_mva | winter_load_yr2_poe50_mva | winter_load_yr3_poe50_mva | winter_load_yr4_poe50_mva | winter_load_yr5_poe50_mva | winter_load_yr6_poe50_mva | winter_load_yr7_poe50_mva | winter_load_yr8_poe50_mva | winter_load_yr9_poe50_mva | winter_load_yr10_poe50_mva | winter_load_yr1_poe10_mva | winter_load_yr2_poe10_mva | winter_load_yr3_poe10_mva | winter_load_yr4_poe10_mva | winter_load_yr5_poe10_mva | winter_load_yr6_poe10_mva | winter_load_yr7_poe10_mva | winter_load_yr8_poe10_mva | winter_load_yr9_poe10_mva | winter_load_yr10_poe10_mva | mapped_poe | load_at_risk_yr1_mw | load_at_risk_yr2_mw | load_at_risk_yr3_mw | load_at_risk_yr4_mw | load_at_risk_yr5_mw | EUSE_MWh_yr1 | EUSE_MWh_yr2 | EUSE_MWh_yr3 | EUSE_MWh_yr4 | EUSE_MWh_yr5 | EUSE_MWh_yr6 | EUSE_MWh_yr7 | EUSE_MWh_yr8 | EUSE_MWh_yr9 | EUSE_MWh_yr10 | hrs_exceedance_yr1 | hrs_exceedance_yr2 | hrs_exceedance_yr3 | hrs_exceedance_yr4 | hrs_exceedance_yr5 | hrs_exceedance_yr6 | hrs_exceedance_yr7 | hrs_exceedance_yr8 | hrs_exceedance_yr9 | hrs_exceedance_yr10 | EUSE_value_yr1 | EUSE_value_yr2 | EUSE_value_yr3 | EUSE_value_yr4 | EUSE_value_yr5 | EUSE_value_yr6 | EUSE_value_yr7 | EUSE_value_yr8 | EUSE_value_yr9 | EUSE_value_yr10 | summer_support_constraintyr_mw | summer_support_constraintyr_mva | summer_support_yr1_mva | summer_support_yr2_mva | summer_support_yr3_mva | summer_support_yr4_mva | summer_support_yr5_mva | summer_support_yr6_mva | summer_support_yr7_mva | summer_support_yr8_mva | summer_support_yr9_mva | summer_support_yr10_mva | winter_support_constraintyr_mw | winter_support_constraintyr_mva | winter_support_yr1_mva | winter_support_yr2_mva | winter_support_yr3_mva | winter_support_yr4_mva | winter_support_yr5_mva | winter_support_yr6_mva | winter_support_yr7_mva | winter_support_yr8_mva | winter_support_yr9_mva | winter_support_yr10_mva | power_factor | reactive_support_details | load_transfer_capability_mva | emergency_generation_mva | emergency_generation_mw | historic_emergency_generation_flag | connected_region1 | connected_region1_EF | connected_region2 | connected_region2_EF | connected_region3 | connected_region3_EF | connected_region4 | connected_region4_EF | connected_region5 | connected_region5_EF | connected_region6 | connected_region6_EF | connected_region7 | connected_region7_EF | connected_region8 | connected_region8_EF | connected_region9 | connected_region9_EF | connected_region10 | connected_region10_EF | connected_region11 | connected_region11_EF | connected_region12 | connected_region12_EF | connected_region13 | connected_region13_EF | connected_region14 | connected_region14_EF | connected_region15 | connected_region15_EF | connected_region16 | connected_region16_EF | connected_region17 | connected_region17_EF | connected_region18 | connected_region18_EF | connected_region19 | connected_region19_EF | connected_region20 | connected_region20_EF | connected_region21 | connected_region21_EF | connected_region22 | connected_region22_EF | connected_region23 | connected_region23_EF | connected_region24 | connected_region24_EF | connected_region25 | connected_region25_EF | connected_region26 | connected_region26_EF | connected_region27 | connected_region27_EF | connected_region28 | connected_region28_EF | connected_region29 | connected_region29_EF | connected_region30 | connected_region30_EF | template_version_v3.1
| ORS3B2 Jeager Ave |  |  | DF |  | 11 |  | Project will install a switching station in Churchill Avenue adjacent to Electrolux so that the unutilised ORS3B3 Feeder can be used to back up ORS3B8 Edward Street and ORS3B5 Lords Place for network reliability |  | -33.2963 | 149.1027 | -33.2963 | 149.1027 | 736 | 1 | Reliability | 251707 |  |  |  | 251707 | 0.1 | 0.1 | 18405 |  | 5034 | 06/2025 | [7 empty] | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | [15 empty] | 3.02 | 3.06 | 3.09 | 3.12 | 3.15 | [7 empty] | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | [15 empty] | 3.02 | 3.06 | 3.09 | 3.12 | 3.15 | [6 empty] | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 3.7 | 0 |  | No
| ORS3B3 Email (Electrolux) |  |  | DF |  | 11 |  | Orange Install 3 way switching station |  | -33.3037 | 149.0978 | -33.3037 | 149.0978 | 988 | 1 | Reliability | 203709 |  |  |  | 203709 | 0.1 | 0.1 | 14896 |  | 4074 | 06/2024 | [7 empty] | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | [15 empty] | 0 | 0 | 0 | 0 | 0 | [7 empty] | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | [15 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| ORS3B5 Lords Place |  |  | DF |  | 11 |  | Millthorpe-BurtonsLn&WilsonsLn-HVReconductoring-Refurb |  | -33.4459 | 149.1022 | -33.4859 | 149.0682 | 1120 | 0.16 | Asset Condition |  | 276936 |  |  | 276936 | 0.1 | 0.1 | 20250 |  | 5539 | 07/2024 | [7 empty] | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | [15 empty] | 3.21 | 3.24 | 3.28 | 3.31 | 3.35 | [7 empty] | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | [15 empty] | 3.21 | 3.24 | 3.28 | 3.31 | 3.35 | [6 empty] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 1.33 | 0 |  | No
| BNY3B4 Millthorpe |  |  | DF |  | 11 |  | Bathurst supply constraints BTH3B7 Llyods Rd Feeder |  | -33.4419 | 149.5689 | -33.4612 | 149.5716 | 141 | 0.8 | Capacity | 251258 |  |  |  | 251258 | 0.1 | 0.1 | 18373 |  | 5025 | 06/2025 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [6 empty] | 2.74 | 2.7 | 2.7 | 2.7 | 2.7 | 2.74 | 2.7 | 2.7 | 2.7 | 2.7 | [26 empty] | 1.6 | [11 empty] | 1.6 | [10 empty] | 0.95 |  | 0.48 | 0 |  | No
| BTH3B8 Lagoon/Trunkey |  |  | DF |  | 11 |  | Bathurst voltage constraints Raglan 3B3 |  | -33.4264 | 149.72 | -33.4278 | 149.7535 | 267 | 0.26 | Voltage | 200504 |  |  |  | 200504 | 0.1 | 0.1 | 14661 |  | 4010 | 06/2024 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.5 | [11 empty] | 0.5 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| BNY3B4 Millthorpe |  |  | DF |  | 22 |  | Berrigan, Tocumwal FIN8B1 upgrade regulator 62-V602 to 300A & install additional recloser north of Fullers Rd Finley . |  | -35.7078 | 145.5776 | -35.8785 | 145.6596 | 1927 | 1 | Capacity | 598481 |  |  |  | 598481 | 0.1 | 0.1 | 43762 |  | 11970 | 06/2025 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [6 empty] | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| RAG3B6 Limekilns |  |  | DF |  | 22 |  | Albury, Catherine Cres, sub 61-50317 replace failed HV ring main switch & damaged HV cable, def Rec |  | -36.0414 | 146.9651 | -36.0419 | 146.9626 | 941 | 1 | Asset Condition |  | 316713 |  |  | 316713 | 0.1 | 0.1 | 23159 |  | 6334 | 06/2024 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 3.06 | 3.08 | 3.09 | 3.1 | 3.12 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 3.06 | 3.08 | 3.09 | 3.1 | 3.12 | [6 empty] | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| SWT42 Simplot |  |  | DF |  | 22 |  | Install a new 22kV line along Dandaloo Rd. |  | -32.375 | 147.4872 | -32.2606 | 147.6244 | 856 | 0.6 | Reliability | 1784443 |  |  |  | 1784443 | 0.1 | 0.1 | 130482 |  | 35689 | 06/2025 | [7 empty] | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | [15 empty] | 5.82 | 5.9 | 5.96 | 6.04 | 6.15 | [7 empty] | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | [15 empty] | 5.82 | 5.9 | 5.96 | 6.04 | 6.15 | [6 empty] | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.991 |  | 0.5 | 0 |  | No
| BTH3B7 Lloyds Rd |  |  | DF |  | 11 |  | Parkes Porter St Replace failed LV cables |  | -33.1453 | 148.178 | -33.1465 | 148178685 | 2054 | 0.01 | Asset Condition |  | 564270 |  |  | 564270 | 0.1 | 0.1 | 41261 |  | 11285 | 06/2025 | [7 empty] | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | [15 empty] | 3.87 | 3.87 | 3.87 | 3.86 | 3.86 | [7 empty] | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | [15 empty] | 3.87 | 3.87 | 3.87 | 3.86 | 3.86 | [6 empty] | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| BTH3B6 City Central |  |  | DF |  | 11 |  | Reedy Swamp Reedy Swamp Rd Replace 6km in poor condition 7/0.064 SC/GZ. |  | -36.679 | 149.8724 | -36.7015 | 149.8838 | 1549 | 0.03 | Asset Condition |  | 284493 |  |  | 284493 | 0.1 | 0.1 | 20803 |  | 5690 | 06/2024 | [7 empty] | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | [15 empty] | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | [7 empty] | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | [15 empty] | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | [6 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| FIN8B1 Tocumwal |  |  | DF |  | 22 |  | Bogan Gate Henry Parkes Way Replace failing HDBC conductor. |  | -33.1098 | 147.761 | -33.1141 | 147.6888 | 203 | 0.09 | Asset Condition |  | 283687 |  |  | 283687 | 0.1 | 0.1 | 20744 |  | 5674 | 06/2025 | [7 empty] | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | [15 empty] | 5.36 | 5.38 | 5.38 | 5.39 | 5.39 | [7 empty] | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | [15 empty] | 5.36 | 5.38 | 5.38 | 5.39 | 5.39 | [6 empty] | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| MWA8B4 North St and Rural |  |  | DF |  | 22 |  | Tullamore Switching Station Upgrade Feeder Protection on 11kV Network |  | -32.6528 | 147.5816 | -32.654 | 147.5808 | 856 | 1 | Reliability |  | 219269 |  |  | 219269 | 0.1 | 0.1 | 16033 |  | 4385 | 06/2025 | [7 empty] | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | [15 empty] | 2 | 2 | 2 | 2 | 2.02 | [7 empty] | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | [15 empty] | 2 | 2 | 2 | 2 | 2.02 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.991 |  | 0 | 0 |  | No
| CRA42 Corurgan |  |  | DF |  | 11 |  | Goonumbla Wards Ln Replace faulty conductor |  | -32.9715 | 148.1658 | -32.9828 | 148.222 | 945 | 0.01 | Asset Condition |  | 214002 |  |  | 214002 | 0.1 | 0.1 | 15648 |  | 4280 | 06/2025 | [7 empty] | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | [15 empty] | 3.19 | 3.2 | 3.2 | 3.2 | 3.22 | [7 empty] | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | [15 empty] | 3.19 | 3.2 | 3.2 | 3.2 | 3.22 | [6 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| HOL1890 Wantagong/Woomargama |  |  | DF |  | 11 |  | Moruya Phyllis Price Dr Replace 31-V1471 with Coopers Regs |  | -35.877 | 150.1178 | -35.877 | 150.1178 | 1233 | 0.03 | Asset Condition |  | 205697 |  |  | 205697 | 0.1 | 0.1 | 15041 |  | 4114 | 06/2025 | [7 empty] | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | [15 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.86 | [7 empty] | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | [15 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.86 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 2 | 0 |  | No
| BOM8B2 Nimmitabel |  |  | DF |  | 11 |  | New 11kV feeder as a dedicated supply to Berridale township, freeing up existing feeder as a dedicated supply for Kalkite |  | -36.39 | 148.6719 | -36.3637 | 148.7282 | 1159 | 1 | Capacity | 712398 |  |  |  | 712398 | 0.2 | 0.2 | 52092 |  | 14248 | 06/2025 | [7 empty] | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | [15 empty] | 0.28 | 0.29 | 0.29 | 0.29 | 0.29 | [7 empty] | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | [15 empty] | 0.28 | 0.29 | 0.29 | 0.29 | 0.29 | [6 empty] | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | [26 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  | 0.45 | 0 |  | No
| JYE3B2 Kalkite |  |  | DF |  | 11 |  | Replace failing Quince conductor with Raisin |  | -34.8278 | 149.5594 | -34.8794 | 149.5278 | 2390 | 0.01 | Asset Condition |  | 321532 |  |  | 321532 | 0.1 | 0.1 | 23511 |  | 6430 | 06/2024 | [7 empty] | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | [15 empty] | 2.76 | 2.82 | 2.87 | 2.93 | 3 | [7 empty] | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | [15 empty] | 2.76 | 2.82 | 2.87 | 2.93 | 3 | [6 empty] | 2 | 2.5 | 3 | 3.5 | 3.5 | 2 | 2.5 | 3 | 3.5 | 3.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| ADE22 Rural West |  |  | DF |  | 22 |  | Replace failing Quince conductor and install 2 reclosers to improve reliability |  | -34.7295 | 149.8226 | -34.6929 | 149.852 | 656 | 0.14 | Asset Condition |  | 290087 |  |  | 290087 | 0.1 | 0.1 | 21212 |  | 5801 | 11/2024 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.47 | 0.47 | 0.47 | 0.47 | 0.48 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.47 | 0.47 | 0.47 | 0.47 | 0.48 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| MTG4B1 Tibooburra Backbone Line |  |  | DF |  | 11 |  | Reconductor from 2454 084 to reclosers 70-R80 and 70-R382 with Flourine. |  | -33.399 | 148.6091 | -33.3575 | 148.6091 | 706 | 0.12 | Voltage | 370000 | 170000 |  |  | 540000 | 0.1 | 0.1 | 39486 |  | 10800 | 06/2025 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.34 | 1.36 | 1.38 | 1.4 | 1.4 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.34 | 1.36 | 1.38 | 1.4 | 1.4 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0.05 | [11 empty] | 0.05 | [10 empty] | 1 |  | 0.1 | 0 |  | No
| TDL8B2 Tullamore/Tottenham |  |  | DF |  | 22 |  | Relocate Step up transformer and 22 to 11kV conversion |  | -33.3808 | 147.6616 | -33.5472 | 147.656 | 179 | 1 | Reliability | 373774 |  |  |  | 373774 | 0.1 | 0.1 | 27331 |  | 7475 | 06/2025 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [6 empty] | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| YAS6242 Yass Town Sth |  |  | DF |  | 11 |  | Replacement of 7/064HDCU mainline conductor |  | -33.3625 | 147.6728 | -33.3211 | 147.5892 | 101 | 1 | Asset Condition |  | 336973 |  |  | 336973 | 0.1 | 0.1 | 24640 |  | 6739 | 07/2023 | [7 empty] | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | [15 empty] | 4.43 | 4.46 | 4.49 | 4.52 | 4.57 | [7 empty] | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | [15 empty] | 4.43 | 4.46 | 4.49 | 4.52 | 4.57 | [6 empty] | 0.06 | 0.1 | 0.06 | 0.06 | 0.06 | 0.06 | 0.1 | 0.06 | 0.06 | 0.06 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| WGN72 Yeoval |  |  | DF |  | 33 |  | Upgrade Darlington Pt Farms CLY1523 Bore Pumpers 33kV tie ( Griffith Network) OH Conductors |  | -34.6199 | 145.9018 | -34.5486 | 145.9097 | 55 | 0.56 | Capacity | 619083 |  |  |  | 619083 | 0.1 | 0.1 | 45269 |  | 12381 | 06/2025 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [6 empty] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| TDL8B2 Tullamore/Tottenham |  |  | DF |  | 11 |  | Griffith Whites Rd Reconductor 4km |  | -34.2642 | 146.0005 | -34.2497 | 145.9731 | 261 | 0.25 | Asset Condition |  | 339002 |  |  | 339002 | 0.1 | -0.1 | 24789 |  | 6780 | 06/2025 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [6 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| PKT3B9 Parkes Town No.3 |  |  | DF |  | 11 |  | Griffith KoobaBetts 96-797 LV Encroachment(West) |  | -34.2791 | 146.0436 | -34.2791 | 146.043 | 1027 | 0.01 | Safety | 216749 |  |  |  | 216749 | 0.1 | 0.1 | 15849 |  | 4334 | 06/2025 | [7 empty] | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | [15 empty] | 5.01 | 5.05 | 5.09 | 5.11 | 5.11 | [7 empty] | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | [15 empty] | 5.01 | 5.05 | 5.09 | 5.11 | 5.11 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| WJL3B3 West Plain |  |  | DF |  | 22 |  | Leeton Corbie Hill Payten Rd Reconductor cu 4.5km |  | -34.5577 | 146.4586 | -34.5942 | 146.4719 | 799 | 0.15 | Voltage | 211210 |  |  |  | 211210 | 0.1 | 0.1 | 15444 |  | 4224 | 06/2025 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.78 | 0.78 | 0.78 | 0.78 | 0.77 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.78 | 0.78 | 0.78 | 0.78 | 0.77 | [6 empty] | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| CMK4005 West |  |  | DF |  | 11 |  | Relocate Padmount Sub - Wagga Depot Hammond Ave |  | -35.12 | 147.384 | -35.12 | 147.384 | 296 | 1 | Asset Condition |  | 341000 |  |  | 341000 | 0.1 | 0.1 | 24935 |  | 6823 | 06/2025 | [7 empty] | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | [15 empty] | 0.42 | 0.42 | 0.43 | 0.43 | 0.43 | [7 empty] | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | [15 empty] | 0.42 | 0.42 | 0.43 | 0.43 | 0.43 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| THA2223 West End |  |  | DF |  | 11 |  | LV UG Replacement CONSAC - 71-3456, Adams St Ashmont - Wagga |  | -35.1232 | 147.3215 | -35.1232 | 147.3215 | 1258 | 1 | Asset Condition |  | 247000 |  |  | 247000 | 0.1 | 0.1 | 18061 |  | 4951 | 06/2024 | [7 empty] | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | [15 empty] | 3.41 | 3.43 | 3.44 | 3.45 | 3.45 | [7 empty] | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | [15 empty] | 3.41 | 3.43 | 3.44 | 3.45 | 3.45 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| GFH3B2 Wakaden St |  |  | DF |  | 11 |  | Orange cable replacements Orange South Zone Feeders 10000924 |  | -33.2982 | 149.096 | -33.2984 | 149.0918 | 2412 | 1 | Asset Condition |  | 765314 |  |  | 765314 | 0.1 | 0.1 | 55961 |  | 15306 | 06/2025 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| GFH3B6 Illilliwa |  |  | DF |  | 11 |  | Tamworth, New Winton Rd, Old 66kV structures operating at 11kV |  | -31.093 | 150.845 | -31.0876 | 150.8215 | 33 | 1 | Asset Condition |  | 408829 |  |  | 408829 | 0.1 | 0.1 | 29894 |  | 8177 | 06/2024 | [7 empty] | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | [15 empty] | 4.14 | 4.12 | 4.14 | 4.12 | 4.09 | [7 empty] | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | [15 empty] | 4.14 | 4.12 | 4.14 | 4.12 | 4.09 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| BEE1347 Collina No.1 |  |  | DF |  | 11 |  | Barraba Woodsreef 614614 Asbestos |  | -30.3987 | 150.7282 | -30.3987 | 150.73 | 810 | 0.026 | Safety |  | 306352 |  |  | 306352 | 0.1 | 0.1 | 22401 |  | 6127 | 06/2025 | [7 empty] | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | [15 empty] | 3.86 | 3.94 | 4.04 | 4.11 | 4.17 | [7 empty] | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | [15 empty] | 3.86 | 3.94 | 4.04 | 4.11 | 4.17 | [6 empty] | 3.66 | 3.75 | 3.84 | 3.91 | 3.96 | 3.66 | 3.75 | 3.84 | 3.91 | 3.96 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| GFH3B2 Wakaden St |  |  | DF |  | 11 |  | Tamworth Links Ave 18-15760 LV Consac End of Life |  | -31.1088 | 150.9077 | -31.1088 | 150.9077 | 1493 | 0.023 | Asset Condition |  | 249411 |  |  | 249411 | 0.1 | 0.1 | 18237 |  | 4988 | 06/2024 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| KOO3B1 Plumpton Rd |  |  | DF |  | 22 |  | Inverell MT Russel Rd 30201248 to 30201460 Asset Condition |  | -29.6904 | 150.9419 | -29.6725 | 150.9013 | 706 | 0.092 | Asset Condition | 248616 |  |  |  | 248616 | 0.1 | 0.1 | 18179 |  | 4972 | 06/2025 | [7 empty] | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | [15 empty] | 4.22 | 4.27 | 4.35 | 4.39 | 4.4 | [7 empty] | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | [15 empty] | 4.22 | 4.27 | 4.35 | 4.39 | 4.4 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| ASM3B9 Ashmont Sth |  |  | DF |  | 22 |  | Inverell Gum Flat 30200535 to 30200616 Asset Condition |  | -29.7798 | 150.9836 | -29.7798 | 150.9836 | 706 | 0.147 | Asset Condition |  | 245446 |  |  | 245446 | 0.1 | 0.1 | 17948 |  | 4909 | 06/2025 | [7 empty] | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | [15 empty] | 2.67 | 2.66 | 2.68 | 2.7 | 2.73 | [7 empty] | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | [15 empty] | 2.67 | 2.66 | 2.68 | 2.7 | 2.73 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| HAM3B7 Tarcutta St |  |  | DF |  | 11 |  | UG - Create 11 kV link Spinifex Ave Tea Gardens 88-82432, 1600 m |  | -32.6512 | 152.1487 | -32.6608 | 152.1375 | 1295 | 0.309 | Reliability | 809947 |  |  |  | 809947 | 0.1 | 0.1 | 59225 |  | 16199 | 06/2025 | [7 empty] | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | [15 empty] | 1.63 | 1.66 | 1.69 | 1.72 | 1.75 | [7 empty] | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | [15 empty] | 1.63 | 1.66 | 1.69 | 1.72 | 1.75 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| TAL1414 Talbingo Town |  |  | DF |  | 11 |  | Old Bar Wyden St 29751 Cable Replacement Growth Thermal |  | -31.9734 | 152.5793 | -31.9678 | 152.5804 | 1132 | 0.443 | Capacity | 350272 |  |  |  | 350272 | 0.1 | 0.1 | 25613 |  | 7005 | 06/2025 | [7 empty] | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | [15 empty] | 0.57 | 0.59 | 0.61 | 0.62 | 0.64 | [7 empty] | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | [15 empty] | 0.57 | 0.59 | 0.61 | 0.62 | 0.64 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 0.7 | [11 empty] | 0.7 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| ORS3B7 Anson St Sth |  |  | DF |  | 11 |  | Markwell Newells Creek HV Augmentation Encroachment |  | -32.2909 | 152.1754 | -32.2933 | 152.1749 | 177 | 0.661 | Safety |  | 343998 |  |  | 343998 | 0.1 | 0.1 | 25154 |  | 6880 | 06/2025 | [7 empty] | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | [15 empty] | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | [7 empty] | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | [15 empty] | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | [6 empty] | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| RAG3B5 OConnell |  |  | DF |  | 11 |  | Harrington Bungulla Place CONSAC replacement EOL |  | -31.8725 | 152.6816 | -31.8712 | 152.6803 | 1033 | 0.042 | Asset Condition |  | 325367 |  |  | 325367 | 0.1 | 0.1 | 23792 |  | 6507 | 06/2025 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.53 | 1.54 | 1.55 | 1.56 | 1.56 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.53 | 1.54 | 1.55 | 1.56 | 1.56 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| DNO132 Dunedoo No.1 |  |  | DF |  | 11 |  | Armidale Rologas Flats Sub 16-1466 End of Life |  | -30.5144 | 151.6688 | -30.5144 | 151.6688 | 774 | 0.068 | Asset Condition |  | 525742 |  |  | 525742 | 0.1 | 0.1 | 38443 |  | 10515 | 06/2024 | [7 empty] | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | [15 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | [15 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| ETH3B7 TCC/Calala |  |  | DF |  | 11 |  | Armidale, Rokvale North, 16-R12142, HV Reconductor. |  | -30.3088 | 152.0261 | -30.324 | 152.107 | 207 | 0.087 | Reliability |  | 429480 |  |  | 429480 | 0.1 | 0.1 | 31405 |  | 8590 | 06/2025 | [7 empty] | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | [15 empty] | 6.4 | 6.4 | 6.5 | 6.4 | 6.4 | [7 empty] | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | [15 empty] | 6.4 | 6.4 | 6.5 | 6.4 | 6.4 | [6 empty] | 4.8 | 4.85 | 4.9 | 4.95 | 4.99 | 4.8 | 4.85 | 4.9 | 4.95 | 4.99 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| GDH8B15 Sth Gunnedah |  |  | DF |  | 11 |  | Lismore Winterton and Alexandra Pde OH - Reconduct HV |  | -28.802 | 153.2757 | -28.7891 | 153.2892 | 930 | 1 | Asset Condition |  | 322226 |  |  | 322226 | 0.1 | 0.1 | 23562 |  | 6445 | 06/2025 | [7 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [15 empty] | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | [7 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [15 empty] | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | [6 empty] | 0.59 | 0.61 | 0.63 | 0.65 | 0.67 | 0.59 | 0.61 | 0.63 | 0.65 | 0.67 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WCK516 Dewhurst/Gordon |  |  | DF |  | 22 |  | Guyra, Tenterden Rd, HV Reco, Riliability, EOL |  | -30.1195 | 151.5102 | -33.3037 | 149.0978 | 156 | 0.385 | Reliability |  | 285925 |  |  | 285925 | 0.1 | 0.1 | 20907 |  | 5719 | 06/2025 | [7 empty] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | [15 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [7 empty] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | [15 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [6 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| BBA3B4 Barraba |  |  | DF |  | 11 |  | Murwillumbah Buchanan St create HV interconnector MWN3B2/9 |  | -28.3389 | 153.4191 | -28.3373 | 153.4094 | 1101 | 1 | Capacity | 386455 |  |  |  | 386455 | 0.1 | 0.1 | 28258 |  | 7729 | 06/2025 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [15 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [15 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 3 | [11 empty] | 3 | [10 empty] | 0.9 |  | 3 | 0 |  | No
| ATA3B1 Attunga |  |  | DF |  | 11 |  | Tweed Heads South Alf Rush Memorial Dr Sub 54-212 EOL Chamber sub replacement |  | -28.2089 | 153.5592 | -28.2089 | 153.5592 | 1968 | 0.001 | Asset Condition |  | 349243 |  |  | 349243 | 0.1 | 0.1 | 25537 |  | 6985 | 06/2025 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [6 empty] | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| BGA2K13 Horton Valley |  |  | DF |  | 11 |  | Kunghur Kyogle Rd 6.4km 11kV Reconductor Reliability |  | -28.4909 | 153.2177 | -28.4654 | 153.2657 | 2132 | 0.077 | Asset Condition |  | 301257 |  |  | 301257 | 0.1 | 0.1 | 22029 |  | 6025 | 06/2025 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 0.37 | 0.37 | 0.37 | 0.38 | 0.38 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 0.37 | 0.37 | 0.37 | 0.38 | 0.38 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| MRE8B4 Western Rural |  |  | DF |  | 11 |  | Lawrence River Crossing Pole 74700 End Of Life |  | -29.4916 | 153.1172 | -29.4916 | 153.1172 | 857 | 0.9 | Safety |  | 261415 |  |  | 261415 | 0.1 | 0.1 | 19115 |  | 5228 | 06/2025 | [7 empty] | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | [15 empty] | 4.02 | 4.13 | 5.7 | 6.29 | 5.57 | [7 empty] | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | [15 empty] | 4.02 | 4.13 | 5.7 | 6.29 | 5.57 | [6 empty] | 3.9 | 4 | 5.6 | 6.2 | 5.5 | 3.9 | 4 | 5.6 | 6.2 | 5.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WTR8B2 Poison Gate |  |  | DF |  | 11 |  | Gilgandra Main Street Under Awning Fascia LV Mains |  | -31.7122 | 148.6682 | -31.7106 | 148.6698 | 770 | 0.013 | Safety |  | 716024 |  |  | 716024 | 0.1 | 0.1 | 52357 |  | 14320 | 06/2024 | [7 empty] | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | [15 empty] | 3.54 | 3.52 | 3.53 | 3.53 | 3.53 | [7 empty] | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | [15 empty] | 3.54 | 3.52 | 3.53 | 3.53 | 3.53 | [6 empty] | 3.38 | 3.36 | 3.37 | 3.37 | 3.36 | 3.38 | 3.36 | 3.37 | 3.37 | 3.36 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0.2 | 0 |  | No
| BNK24787 Old Bar No.2 |  |  | DF |  | 11 |  | Dubbo Eulomogo ZS CB32 CB82 Replace HV UG Cable |  | -32.2512 | 148.6482 | -32.2512 | 148.6482 | 1490 | 1 | Asset Condition |  | 523415 |  |  | 523415 | 0.1 | 0.1 | 38273 |  | 10468 | 06/2024 | [7 empty] | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | [15 empty] | 2.09 | 2.14 | 2.19 | 2.23 | 2.27 | [7 empty] | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | [15 empty] | 2.09 | 2.14 | 2.19 | 2.23 | 2.27 | [6 empty] | 2.09 | 2.14 | 2.18 | 2.22 | 2.26 | 2.09 | 2.14 | 2.18 | 2.22 | 2.26 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| BLH3B3 Bulahdelah Nth/Markwell/Newells Ck |  |  | DF |  | 11 |  | Dubbo Windsor Pde CE261523 End of Life |  | -32.256 | 148.6423 | -32.2579 | 148.6389 | 1170 | 0.065 | Asset Condition |  | 257090 |  |  | 257090 | 0.1 | 0.1 | 18799 |  | 5142 | 06/2024 | [7 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [15 empty] | 1.66 | 1.67 | 1.69 | 1.71 | 1.73 | [7 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [15 empty] | 1.66 | 1.67 | 1.69 | 1.71 | 1.73 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| HGN3B1 Crowdy Head |  |  | DF |  | 11 |  | Dubbo Airport U/G 185mm Thermal Constraint 598m |  | -32.2261 | 148.5682 | -32.2223 | 148.5637 | 384 | 0.13 | Capacity | 249806 |  |  |  | 249806 | 0.1 | 0.1 | 18266 |  | 4996 | 06/2025 | [7 empty] | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | [15 empty] | 0.81 | 0.83 | 0.86 | 0.88 | 0.9 | [7 empty] | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | [15 empty] | 0.81 | 0.83 | 0.86 | 0.88 | 0.9 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WTE3B7 Spence St |  |  | DF |  | 11 |  | Gilgandra GID22-1 22 kV OH Conductor End of Life |  | -31.7263 | 148.6552 | -31.7263 | 148.6552 | 609 | 1 | Asset Condition |  | 235374 |  |  | 235374 | 0.1 | 0.1 | 17211 |  | 4707 | 06/2025 | [7 empty] | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | [15 empty] | 3.38 | 3.35 | 3.35 | 3.34 | 3.34 | [7 empty] | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | [15 empty] | 3.38 | 3.35 | 3.35 | 3.34 | 3.34 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| TEA3B4 Tea Gardens |  |  | DF |  | 11 |  | 11kV Feeder backup Pacific Highway, Halfway Creek, Voltage |  | -29.9514 | 153.1183 | -29.9642 | 153.1322 | 1226 | 0.8 | Reliability | 667008 |  |  |  | 667008 | 0.1 | 0.1 | 48773 |  | 13340 | 06/2025 | [7 empty] | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | [15 empty] | 2.72 | 2.74 | 2.75 | 2.75 | 2.74 | [7 empty] | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | [15 empty] | 2.72 | 2.74 | 2.75 | 2.75 | 2.74 | [6 empty] | 2.72 | 2.73 | 2.74 | 2.74 | 2.73 | 2.72 | 2.73 | 2.74 | 2.74 | 2.73 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 1 | 0 |  | No
| GLS3B2 Rockvale |  |  | DF |  | 11 |  | OH-11kV - Establish new river crossing -270m- Broadwater |  | -28.9965 | 153.443 | -28.9965 | 153.4434 | 376 | 0.133 | Voltage |  |  | 594675 |  | 594675 | 0.1 | 0.1 | 43484 |  | 11894 | 06/2024 | [7 empty] | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | [15 empty] | 1.77 | 1.8 | 1.82 | 1.84 | 1.86 | [7 empty] | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | [15 empty] | 1.77 | 1.8 | 1.82 | 1.84 | 1.86 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WLS3B1 Walcha East |  |  | DF |  | 11 |  | UG-11kV - replace 95mm cable - 360m - Hutley Dve, Lennox Hd |  | -28.8022 | 153.5857 | -28.8012 | 153.5885 | 673 | 1 | Capacity | 296482 |  |  |  | 296482 | 0.1 | 0.1 | 21679 |  | 5930 | 06/2025 | [7 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | [15 empty] | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | [7 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | [15 empty] | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | [6 empty] | 0.01 | 0 | 0.2 | 0.21 | 0.2 | 0.01 | 0 | 0.2 | 0.21 | 0.2 | [26 empty] | 0.5 | [11 empty] | 0.5 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| HGE3B1 Grafton Rd |  |  | DF |  | 11 |  | Port Macquarie Central Rd & Acacia Ave Conductor Rating |  | -31.4538 | 152.8819 | -31.4547 | 152.8802 | 1069 | 0.047 | Capacity | 642466 |  |  |  | 642466 | 0.1 | 0.1 | 46979 |  | 12849 | 06/2024 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.27 | 0.27 | 0.28 | 0.28 | 0.28 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.27 | 0.27 | 0.28 | 0.28 | 0.28 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.1 | [11 empty] | 0.1 | [10 empty] | 0.9 |  | 0.1 | 0 |  | No
| GLS3B7 City Central |  |  | DF |  | 11 |  | HV UG DEFRECT replace HV cable 400m McLaren Drv nr sub 2-41451 Port Macquarie |  | -31.4489 | 152.9086 | -31.4496 | 152.9136 | 1370 | 0.182 | Asset Condition |  | 282896 |  |  | 282896 | 0.1 | 0.1 | 20686 |  | 5658 | 06/2024 | [7 empty] | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | [15 empty] | 2.07 | 2.11 | 2.13 | 2.15 | 2.18 | [7 empty] | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | [15 empty] | 2.07 | 2.11 | 2.13 | 2.15 | 2.18 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| MLN3B4 Townsend |  |  | DF |  | 11 |  | Port Macquarie Highfields Cct Conductor Rating |  | -31.4538 | 152.8819 | -31.4547 | 152.8802 | 1069 | 0.05 | Capacity | 226711 |  |  |  | 226711 | 0.1 | 0.1 | 16578 |  | 4534 | 06/2024 | [7 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [15 empty] | 2.47 | 2.48 | 2.49 | 2.47 | 2.42 | [7 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [15 empty] | 2.47 | 2.48 | 2.49 | 2.47 | 2.42 | [6 empty] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | [26 empty] | 0.1 | [11 empty] | 0.1 | [10 empty] | 0.9 |  | 0.1 | 0 |  | No
| SGN3B4 Ulmarra |  |  | DF |  | 11 |  | OH_2480m 1ph 11kV 3/2.75SC/GZ Reconduct_Freedom Island |  | -30.8851 | 153.0061 | -30.8671 | 152.9927 | 862 | 0.01 | Asset Condition |  | 219213 |  |  | 219213 | 0.1 | 0.1 | 16029 |  | 4384 | 06/2025 | [7 empty] | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | [15 empty] | 2.1 | 2.09 | 2.09 | 2.09 | 2.08 | [7 empty] | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | [15 empty] | 2.1 | 2.09 | 2.09 | 2.09 | 2.08 | [6 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| MWN3B8 Uki |  |  | DF |  | 11 |  | Kunghur Doon Doon Rd 11kV Reconductor End Of Life |  | -28.4663 | 153.2665 | -28.5033 | 153.2651 | 2136 | 0.06 | Asset Condition |  | 277299 |  |  | 277299 | 0.1 | 0.1 | 22578 |  | 5585 | 06/2026 | [7 empty] | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | [15 empty] | 3.39 | 3.41 | 3.42 | 3.45 | 3.48 | [7 empty] | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | [15 empty] | 3.39 | 3.41 | 3.42 | 3.45 | 3.48 | [6 empty] | 3.25 | 3.27 | 3.29 | 3.31 | 3.34 | 3.25 | 3.27 | 3.29 | 3.31 | 3.34 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| SGN3B1 Armidale Rd |  |  | DF |  | 11 |  | Wells Crossing Parker Rd Establish HV Tie Reliability |  | -29.9081 | 153.023 | -29.9075 | 153.0649 | 1231 | 0.29 | Reliability | 458005 |  |  |  | 458005 | 0.1 | 0.1 | 37292 |  | 9160 | 06/2025 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [6 empty] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| MLN3B5 Woodford Dale-Leigh |  |  | DF |  | 11 |  | Lawrence River Crossing Pole 74700 End Of Life |  | -29.4916 | 153.1172 | -29.4916 | 153.1172 | 863 | 0.72 | Safety |  | 282348 |  |  | 282348 | 0.1 | 0.1 | 22989 |  | 5647 | 06/2026 | [7 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [15 empty] | 1.59 | 1.59 | 1.6 | 1.59 | 1.56 | [7 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [15 empty] | 1.59 | 1.59 | 1.6 | 1.59 | 1.56 | [6 empty] | 1.55 | 1.56 | 1.57 | 1.55 | 1.53 | 1.55 | 1.56 | 1.57 | 1.55 | 1.53 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 1 | 0 |  | No
| MWN3B2 Norco |  |  | DF |  | 11 |  | Murwillumbah Buchanan St create HV interconnector MWN3B2/9 |  | -28.3373 | 153.4094 | -28.3386 | 153.4192 | 1105 | 1 | Capacity | 414506 |  |  |  | 414506 | 0.1 | 0.1 | 33750 |  | 8022 | 06/2025 | [7 empty] | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | [15 empty] | 2.55 | 2.57 | 2.58 | 2.6 | 2.63 | [7 empty] | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | [15 empty] | 2.55 | 2.57 | 2.58 | 2.6 | 2.63 | [6 empty] | 2.45 | 2.47 | 2.48 | 2.5 | 2.52 | 2.45 | 2.47 | 2.48 | 2.5 | 2.52 | [26 empty] | 2 | [11 empty] | 2 | [10 empty] | 0.96 |  | 1 | 0 |  | No
| BPT3B3 Fingal |  |  | DF |  | 11 |  | Tweed Heads South Alf Rush Memorial Dr Sub 54-212 EOL Chamber sub replacement |  | -28.2077 | 153.5606 | -28.2077 | 153.5606 | 1972 | 0.01 | Asset Condition | 370791 |  |  |  | 370791 | 0.1 | 0.1 | 30191 |  | 6908 | 06/2026 | [7 empty] | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | [15 empty] | 4.46 | 4.46 | 4.46 | 4.47 | 4.48 | [7 empty] | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | [15 empty] | 4.46 | 4.46 | 4.46 | 4.47 | 4.48 | [6 empty] | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| BHL42 Railwaytown |  |  | DF |  | 22 |  | Broken Hill, Refurbishment sub 6-16271 Sturt Park Sulphide St |  | -31.9571 | 141.4625 | -31.9571 | 141.4625 | 4472 | 0.04 | Asset Condition |  | 294685 |  |  | 294685 | 0.1 | 0.1 | 23994 |  | 5894 | 06/2025 | [7 empty] | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | [15 empty] | 40.78 | 42.22 | 42.21 | 42.07 | 41.8 | [7 empty] | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | [15 empty] | 40.78 | 42.22 | 42.21 | 42.07 | 41.8 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.981 |  | 0 | 0 |  | No
| WLC4B1 White Cliffs |  |  | DF |  | 33 |  | Wilcannia - Underground Network alterations White Cliffs |  | -30.8531 | 143.097 | -30.8463 | 143.0836 | 262 | 0.44 | Safety |  | 387059 |  |  | 387059 | 0.1 | 0.1 | 31515 |  | 7741 | 06/2025 | [7 empty] | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | [15 empty] | 0.64 | 0.65 | 0.67 | 0.68 | 0.69 | [7 empty] | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | [15 empty] | 0.64 | 0.65 | 0.67 | 0.68 | 0.69 | [6 empty] | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | [26 empty] | 0.15 | [11 empty] | 0.15 | [10 empty] | 0.857 |  | 0 | 0 |  | No
| DBS3B8 Margaret Cres |  |  | DF |  | 11 |  | Replace existing 1000kVA Pad Sub 30-4559 with a 1500 kVA Pad Sub. |  | -32.26 | 148.6233 | -32.26 | 148.6233 | 2287 | 0 | Capacity |  | 258749 |  |  | 258749 | 0.1 | 0.1 | 21068 |  | 5175 | 06/2025 | [7 empty] | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | [15 empty] | 5.27 | 5.33 | 5.39 | 5.45 | 5.49 | [7 empty] | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | [15 empty] | 5.27 | 5.33 | 5.39 | 5.45 | 5.49 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| BKE4B2 M82 Wanaaring |  |  | DF |  | 33 |  | Bourke Wanaaring BKE4B2 M82 Multiple Sites Poor Performing Feeder |  | -29.3547 | 145.0001 | -29.668 | 145.272 | 331 | 0.8 | Reliability |  | 280710 |  |  | 280710 | 0.1 | 0.1 | 22856 |  | 5614 | 06/2025 | [7 empty] | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | [15 empty] | 1.62 | 1.62 | 1.63 | 1.65 | 1.67 | [7 empty] | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | [15 empty] | 1.62 | 1.62 | 1.63 | 1.65 | 1.67 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.54 |  | 0 | 0 |  | No
| DBW3B5 Rural West |  |  | DF |  | 11 |  | Dubbo Airport U/G 185mm Thermal Constraint 598m |  | -32.2261 | 148.5682 | -32.2222 | 148.5636 | 388 | 1 | Capacity |  | 261645 |  |  | 261645 | 0.1 | 0.1 | 21304 |  | 5233 | 06/2026 | [7 empty] | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | [15 empty] | 2.7 | 2.74 | 2.76 | 2.78 | 2.81 | [7 empty] | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | [15 empty] | 2.7 | 2.74 | 2.76 | 2.78 | 2.81 | [6 empty] | 2.62 | 2.66 | 2.68 | 2.7 | 2.73 | 2.62 | 2.66 | 2.68 | 2.7 | 2.73 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.971 |  | 0 | 0 |  | No
| EUL32 Dubbo Nth/East Town |  |  | DF |  | 11 |  | Replace defective cable emanating from the Eulomogo Zone Substation |  | -32.2517 | 148.6488 | -32.2459 | 148.6487 | 1495 | 1 | Asset Condition |  | 483545 |  |  | 483545 | 0.1 | 0.1 | 39371 |  | 9671 | 06/2025 | [7 empty] | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | [15 empty] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | [7 empty] | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | [15 empty] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | [6 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| GID22 Rural Nth/Sth/West |  |  | DF |  | 11 |  | Replace 2.9 km of 7/104 HDBC 11 kV conductor with 7/450 AAAC in the vicinity of South Gilgandra. |  | -31.7206 | 148.6554 | -31.7418 | 148.6446 | 610 | 1 | Asset Condition |  | 302320 |  |  | 302320 | 0.1 | 0.1 | 24616 |  | 6046 | 06/2026 | [7 empty] | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | [15 empty] | 2.08 | 2.09 | 2.1 | 2.11 | 2.12 | [7 empty] | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | [15 empty] | 2.08 | 2.09 | 2.1 | 2.11 | 2.12 | [6 empty] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.992 |  | 0 | 0 |  | No
| GID12 Gilgandra Town No.1 |  |  | DF |  | 11 |  | Relocate the existing Low Voltage network that supplies the CBD of the Township of Gilgandra |  | -31.7122 | 148.6682 | -31.7106 | 148.6698 | 705 | 0.108 | Safety | 702128 |  |  |  | 702128 | 0.1 | 0.1 | 57169 |  | 14043 | 06/2025 | [7 empty] | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | [15 empty] | 1.95 | 1.96 | 1.97 | 1.98 | 1.99 | [7 empty] | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | [15 empty] | 1.95 | 1.96 | 1.97 | 1.98 | 1.99 | [6 empty] | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| WBN3B3 Coraki |  |  | DF |  | 11 |  | Marom Creek Cook Rd Conductor 4.6km End Of Life |  | -28.897 | 153.3659 | -28.9266 | 153.334 | 914 | 0.01 | Reliability |  | 273485 |  |  | 273485 | 0.1 | 0.1 | 22268 |  | 5470 | 06/2026 | [7 empty] | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | [15 empty] | 1.76 | 1.77 | 1.78 | 1.78 | 1.8 | [7 empty] | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | [15 empty] | 1.76 | 1.77 | 1.78 | 1.78 | 1.8 | [42 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 1 | 0 |  | No | bar: 0.59 to 0.67
| EWE3B1 Brunswick No.1 |  |  | DF |  | 11 |  | Brunswick Heads LV conductor 3.0km End Of Life |  | -28.5424 | 153.5432 | -28.5419 | 153.5539 | 1174 | 0.6 | Asset Condition |  | 433695 |  |  | 433695 | 0.1 | 0.1 | 35312 |  | 8674 | 06/2026 | [7 empty] | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | [15 empty] | 2.1 | 2.13 | 2.16 | 2.19 | 2.24 | [7 empty] | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | [15 empty] | 2.1 | 2.13 | 2.16 | 2.19 | 2.24 | [42 empty] | 1.5 | [11 empty] | 1.5 | [10 empty] | 0.98 |  | 0 | 0 |  | No | bar: 0.59 to 0.67
| WGN72 Yeoval |  |  | DF |  | 11 |  | Wellington, Upgrade conductor beyond 30-R12394, Protection constraints |  | -32.7362 | 148.7431 | -32.8098 | 148.7905 | 373 | 0.12 | Capacity | 598980 |  |  |  | 598980 | 0.1 | 0.1 | 48770 |  | 11980 | 06/2026 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.02 | [11 empty] | 0.02 | [10 empty] | 0.95 |  | 0.01 | 0 |  | No
| TXS3X06 Yelarbon |  |  | DF |  | 33 |  | Texas Holdflat Rd DEF REC 9.8km HV Conductor |  | -28.6697 | 150.6858 | -28.7519 | 150.7042 | 346 | 0.07 | Asset Condition |  | 609577 |  |  | 609577 | 0.1 | 0.1 | 49633 |  | 12192 | 06/2026 | [7 empty] | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | [15 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [7 empty] | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | [15 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [6 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| LKC7781 Cathie Sth |  |  | DF |  | 11 |  | Wallum Drv Seascape Lake Cathie thermal overload & reliability |  | -31566 | 152.827 | -31566 | 152.827 | 1148 | 1 | Reliability | 414450 |  |  |  | 414450 | 0.1 | 0.1 | 33745 |  | 7911 | 06/2029 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 2.08 | 2.16 | 2.24 | 2.32 | 2.41 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 2.08 | 2.16 | 2.24 | 2.32 | 2.41 | [6 empty] | 0.9 | 1.1 | 1.3 | 1.4 | 1.6 | 0.9 | 1.1 | 1.3 | 1.4 | 1.6 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.976 |  | 3 | 0 |  | No
| BPM3B3 Oxley |  |  | DF |  | 11 |  | Port Macquarie Central Rd & Acacia Ave Conductor Rating |  | -31.4511 | 152.875 | -31.455 | 152.874 | 1753 | 0.3 | Capacity | 1021663 |  |  |  | 1021663 | 0.1 | 0.1 | 83186 |  | 20575 | 06/2025 | [7 empty] | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | [15 empty] | 4.15 | 4.22 | 4.3 | 4.38 | 4.45 | [7 empty] | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | [15 empty] | 4.15 | 4.22 | 4.3 | 4.38 | 4.45 | [6 empty] | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | [26 empty] | 0.7 | [11 empty] | 0.7 | [10 empty] | 0.996 |  | 0 | 0 |  | No
| OPM3B1 Granite St |  |  | DF |  | 11 |  | Replace HV cable 400m McLaren Drv near sub 2-41451 Port Macquarie |  | -31.449 | 152.913 | -31.489 | 152.908 | 1372 | 0.054 | Asset Condition |  | 328536 |  |  | 328536 | 0.1 | 0.1 | 26750 |  | 5509 | 06/2024 | [7 empty] | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | [15 empty] | 2.32 | 2.33 | 2.33 | 2.33 | 2.33 | [7 empty] | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | [15 empty] | 2.32 | 2.33 | 2.33 | 2.33 | 2.33 | [6 empty] | 0.51 | 0.51 | 0.5 | 0.5 | 0.5 | 0.51 | 0.51 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| SGN3B1 Armidale Rd |  |  | DF |  | 11 |  | 11kV Feeder backup Pacific Highway, Halfway Creek, Voltage |  | -29.9822 | 153.1429 | -29.9538 | 153.1193 | 1231 | 0.1 | Reliability | 722225 |  |  |  | 722225 | 0.1 | 0.1 | 58805 |  | 14445 | 06/2025 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [6 empty] | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [26 empty] | 0.28 | [11 empty] | 0.28 | [10 empty] | 0.97 |  | 0.5 | 0 |  | No
| GGB112 Gulargambone |  |  | DF |  | 22 |  | Reconductor 7/064 HDBC between GGB112 CB through to 30-G2930 with 7/450 AAAC in vicinity of Gulargambone |  | -31.3253 | 148.4848 | -31.4244 | 148.5254 | 481 | 1 | Asset Condition | 836206 |  |  |  | 836206 | 0.1 | 0.1 | 68086 |  | 16724 | 06/2026 | [7 empty] | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | [15 empty] | 1.31 | 1.31 | 1.32 | 1.32 | 1.32 | [7 empty] | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | [15 empty] | 1.31 | 1.31 | 1.32 | 1.32 | 1.32 | [6 empty] | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| NBI3B1 M14 Spring Ck |  |  | DF |  | 11 |  | Narrabri to Bellata Interconnector supply constraint |  | -30.2384 | 149.8098 | -30.178 | 149.8195 | 81 | 1 | Reliability | 1966866 |  |  |  | 1966866 | 0.1 | 0.1 | 160147 |  | 39337 | 06/2026 | [7 empty] | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | [15 empty] | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | [7 empty] | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | [15 empty] | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.946 |  | 0 | 0 |  | No
| WWA8B4 M8/M21 Spring Plains Rd |  |  | DF |  | 22 |  | WWA8B4 past 75-R602109- Poletop refurb - Poor Performing Feeder |  | -30.1128 | 149.4684 | -29.9673 | 149.4983 | 17 | 0.16 | Reliability | 285987 |  |  |  | 285987 | 0.1 | 0.1 | 23286 |  | 5720 | 06/2026 | [7 empty] | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | [15 empty] | 1.53 | 1.56 | 1.58 | 1.6 | 1.61 | [7 empty] | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | [15 empty] | 1.53 | 1.56 | 1.58 | 1.6 | 1.61 | [6 empty] | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| NBI8B10 M16 Mount Dowe |  |  | DF |  | 22 |  | Replace ground mount TX 75-160005 Mt Dowe Kaputar with padsub |  | -30.2858 | 150.1671 | -30.2858 | 150.1671 | 1 | 0.01 | Reliability |  | 252100 |  |  | 252100 | 0.1 | 0.1 | 20527 |  | 5042 | 06/2025 | [7 empty] | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | [15 empty] | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | [7 empty] | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | [15 empty] | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | [6 empty] | 0.68 | 0.67 | 0.67 | 0.67 | 0.67 | 0.68 | 0.67 | 0.67 | 0.67 | 0.67 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| SFP |  |  | ZS |  | 132 | 11 | Single transformer with high forecast growth |  | -28.6727 | 153.5938 | -28.6727 | 153.5938 | 6400 | 1 | Capacity | 2000000 |  |  |  | 2000000 | 0.1 | 0.1 | 146200 |  | 40000 | 06/2027 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | [15 empty] | 12.6 | 12.9 | 13 | 13.3 | 13.5 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | [15 empty] | 13.8 | 14 | 14.2 | 14.4 | 14.6 | [6 empty] | 13.8 | 14 | 14.2 | 14.4 | 14.6 | 9.66 | 9.8 | 9.94 | 10.08 | 10.22 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 4 | 0
| MRE |  |  | ZS |  | 66 | 22 | Transformer capacity overload with high forecast growth |  | -29.4836 | 149.8519 | -29.4836 | 149.8519 | 6288 | 1 | Capacity | 1000000 |  |  |  | 1000000 | 0.1 | 0.1 | 73100 |  | 20000 | 06/2026 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 90 | 90 | 90 | [15 empty] | 25.3 | 25.9 | 26.4 | 27.3 | 36.4 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 90 | 90 | 90 | [15 empty] | 26.2 | 26.5 | 27.1 | 36.1 | 39.5 | [6 empty] | 26.2 | 26.5 | 27.1 | 36.1 | 39.5 | 18.34 | 18.55 | 18.97 | 25.27 | 27.65 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 4 | 0
| BBN |  |  | ZS |  | 66 | 11 | Transformer capacity overload with high forecast growth |  | -35.0742 | 147.4074 | -35.0742 | 147.4074 | 147 | 1 | Capacity | 2900000 |  |  |  | 2900000 | 0.1 | 0.1 | 211990 |  | 58000 | 06/2026 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | [15 empty] | 11.7 | 11.7 | 11.7 | 15.2 | 21.1 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | [15 empty] | 10.7 | 10.7 | 14.2 | 20.2 | 36.3 | [6 empty] | 11.7 | 11.7 | 14.2 | 20.2 | 36.3 | 8.19 | 8.19 | 9.94 | 14.14 | 25.41 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 8 | 0
| 79W Tharbogang - Warrawidgee - Nericon |  |  | DF |  | 33 |  | Voltage and thermal limitations under contingent conditions |  | -34.2355 | 146.0481 | -34.2039 | 146.0482 | 184 | 1 | Capacity | 4000000 |  |  |  | 4000000 | 0.1 | 0.1 | 292400 |  | 80000 | 06/2027 | [7 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [15 empty] | 11.4 | 11.5 | 11.6 | 11.7 | 11.8 | [7 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [15 empty] | 7.8 | 7.9 | 8 | 8.1 | 8.2 | [6 empty] | 11.4 | 11.5 | 11.6 | 11.7 | 11.8 | 7.98 | 8.05 | 8.12 | 8.19 | 8.26 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 2 | 0